## Raw
AIR TO WATER HEAT PUMP 220V EVI INVERTER |  |  | variable | index | modbus | default | data type | range | note
User parameter settings（User mask） | Electric heating control |  | En_AuxHeat | 0 | 00001 | 0 | bool |  | 0: Day mode; 1: Night mode; 2: Low wind mode; 3: Pressure mode;
| Crankshaft/chassis electric heating control |  | En_Customer_16 | 1 | 00002 | 1 | bool
| Power-off self start |  | OnOffUnitMng.UnitTypAfterPwrOff | 2 | 00003 | 1 | bool
| Working mode |  | CoolHeat_Mode | 0 | 40001 |  | int | 0~5 | 0: Cooling mode; 1: Heating mode; 2: Hot water mode; 3: Hot water+refrigeration; 4: Hot water+heating; 5: Swimming pool
| Heating setting point |  | HeatSetP | 1 | 40002 |  | REAL | 10.0~CoolHeatMng.heat_set_max默认55 | Set value ℃
| Refrigeration setting point |  | CoolSetP | 2 | 40003 |  | REAL | CoolHeatMng.cool_set_min默认12~40.0 | Set value ℃
| Hot water point setting |  | W_TankSetP | 3 | 40004 |  | REAL | 10.0~CoolHeatMng.heat_set_max默认55 | Set value ℃
| Hot water return difference |  | hotwater_start_diff | 4 | 40005 |  | REAL | 1.0~15.0
| Hot water constant temperature shutdown |  | hotwater_stop_diff | 5 | 40006 |  | REAL | 0.0~5.0
| Cooling and heating return difference |  | Temp_Diff | 6 | 40007 |  | REAL | 1.0~15.0
| Refrigeration heating constant temperature shutdown |  | Stop_TemP_Diff | 7 | 40008 |  | REAL | 0.0~5.0
| deviation |  | Kp | 8 | 40009 |  | REAL | 1.0~999.0
| Integral time |  | Ti | 9 | 40010 |  | UINT | 0-9999
| Differential time |  | Td | 10 | 40011 |  | UINT | 0-9999
| Main engine water pump |  | PmpMode | 11 | 40012 |  | int | 0~1 | 0: on; 1: Based on demand;
| Fan mode |  | FanMode_Sel | 12 | 40013 |  | int | 0~3
| Electric heating start delay |  | DT_AuxComp | 13 | 40014 |  | UINT | 0-999
| Electric heating start temperature |  | AuxHeatSetP_Exterior | 14 | 40015 |  | real | -30.0~20.0
| Main water pump control | Speed control inlet and outlet water temperature difference | PmpDeltaTempSetP | 15 | 40016 |  | real | 2.0~15.0
| Heating setting point |  | CFchange.HeatSetP_F | 491 | 40492 |  | REAL | 50.0~CFchange.heat_set_max_F默认131）范围 | Setpoint ℉ added
| Refrigeration setting point |  | CFchange.CoolSetP_F | 492 | 40493 |  | REAL | CFchange.cool_set_min_F（默认53.6）~104范围 | Setpoint ℉ added
| Hot water setting point |  | CFchange.W_TankSetP_F | 493 | 40494 |  | REAL | 50.0~CFchange.heat_set_max_F（默认131）范围 | Setpoint ℉ added
Configure compressor parameters（ BLDC COMPRESSOR） | Low pressure alarm delay | start delay | StartUpDT_SuctLowP | 16 | 40017 |  | int | 0~999
|  | Operation delay | DT_SuctLowPrun | 17 | 40018 |  | int | 0~999
| Speed management | Start-up forced speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_StartUpSpeed | 18 | 40019 |  | REAL | 20.0~120.0
|  | Max speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_MaxSpeedRpsCustom | 19 | 40020 |  | REAL | 0.0~999.0
|  | Min speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_MinSpeedRpsCustom | 20 | 40021 |  | REAL | 0.0~99.0
| Comp BLDC | Out of envelope alarm timeout | BLDC_Mng.CfgEnvCtrl_BLDC1.CstmEnv_EnvOutMaxT | 21 | 40022 |  | INT | 0-32000
|  | Low pressure diff alarm timeout | BLDC_Mng.CfgEnvCtrl_BLDC1.CstmEnv_LowDeltaPAlrmDelay | 22 | 40023 |  | INT | 0-32000
（Manual Control） | Water pump manual |  | En_PmpMan | 3 | 00004 | 0 | BOOL
| Manual speed control fan |  | fan_man_en | 4 | 00005 | 0 | BOOL
| Compressor manual |  | CompMan | 5 | 00006 | 0 | BOOL
| EEV manual |  | EVD_Manual | 6 | 00007 | 0 | BOOL
| Manual four-way valve |  | ManDout3 | 7 | 00008 | 0 | BOOL
| Manual waterway three-way valve |  | ManDout5 | 8 | 00009 | 0 | BOOL
| Manual crankshaft electric heating |  | ManDout6 | 9 | 00010 | 0 | BOOL
| Manual chassis electric heating |  | ManDout7 | 10 | 00011 | 0 | BOOL
| Manual end pump |  | ManDout8 | 11 | 00012 | 0 | BOOL
| Manual electric heating |  | ManDout9 | 12 | 00013 | 0 | BOOL
| Insert frequency converter parameters |  | Insert_POWER | 13 | 00014 | 0 | BOOL
| Manual requirements |  | PmpMan_Aout | 23 | 40024 |  | REAL | 0.0~100.0
| Manual requirements |  | fan_man_out | 24 | 40025 |  | REAL | 0.0~100.0
| Manual requirements |  | ManBLDCPwrReq | 25 | 40026 |  | REAL | 0.0~100.0
| Manual Steps |  | EVD_Manual_Step | 26 | 40027 |  | INT | 0-480
（OTHER PARAMETERS） | Enable upper machine monitoring |  | BmsOnOff_En | 15 | 00016 | 0 | BOOL
| Unit mode |  | en_three_valve | 42 | 00043 | 0 | BOOL |  | 0: Dual supply 1: Triple supply
| Temperature mode |  | Temp_Target_Select | 27 | 40028 |  | INT | 0~1 | 0: Water inlet temperature; 1: Outlet water temperature;
| Protection value of inlet and outlet water temperature difference |  | DeltaTempSetP | 28 | 40029 |  | REAL | 2.0~15.0
| Low water temperature protection value |  | OutLowTempSetP | 29 | 40030 |  | REAL | -99.0~99.0
| High water temperature protection value |  | OutHiTempSetP | 30 | 40031 |  | REAL | -99.0~99.0
| Delay after startup | S | threevlv_delayon | 31 | 40032 |  | INT | 0-999
| Delay before stopping | S | threevlv_delayoff | 32 | 40033 |  | INT | 0-999
| Starting speed of three-way valve |  | PmpSpeedStart | 33 | 40034 |  | REAL | 0.0~100.0
| Three way valve start delay | min | DT_PmpStart | 34 | 40035 |  | INT | 0-999
| Maximum speed |  | PmpMaxSpeed | 35 | 40036 |  | REAL | 0.0~100.0
| Minimum speed |  | PmpMinSpeed | 36 | 40037 |  | REAL | 0.0~100.0
| normally open/normally closed | ID1: Water flow switch | InputsCheck.FlwSw_Logic | 16 | 00017 | 0 | BOOL
|  | ID2: Emergency switch | InputsCheck.RemoteOnOff_Logic | 17 | 00018 | 0 | BOOL
|  | ID3: End signal switch | InputsCheck.Terminal_Switch_Logic | 18 | 00019 | 1 | BOOL
|  | ID5: power phase | InputsCheck.ProtSeqPh_Logic | 19 | 00020 | 0 | BOOL
|  | DO1: High wind | Outputs.FanHiSpeed_Logic | 20 | 00021 | 0 | BOOL
|  | DO2: Low wind | Outputs.FanHiSpeed_Logic | 21 | 00022 | 1 | BOOL
|  | DO3: Four way valve | FwVlv_On_Logic | 22 | 00023 | 0 | BOOL
|  | DO4: Host water pump | Outputs.Pmp_On_Logic | 23 | 00024 | 0 | BOOL
|  | DO5: Waterway three-way valve | Outputs.ThreeWVlv_Logic | 24 | 00025 | 0 | BOOL
|  | DO6: Electric heating of crankshaft | Outputs.HeatCrack_Logic | 25 | 00026 | 0 | BOOL
|  | DO7: Chassis electric heating | Outputs.Heat_Chassis_Logic | 26 | 00027 | 0 | BOOL
|  | DO8: End pump | Outputs.Terminal_Pump_Logic | 27 | 00028 | 0 | BOOL
|  | DO9: Electric heating | Outputs.AuxHeat_Logic | 28 | 00029 | 1 | BOOL
| Probe range | Main valve suction pressure range | nputsCheck.MinVal_SuctP | 37 | 40038 |  | REAL | -99.0~99.0
|  |  | InputsCheck.MaxVal_SuctP | 38 | 40039 |  | REAL | -99.0~99.0
|  | Main valve exhaust pressure range | InputsCheck.MinVal_DscgP | 39 | 40040 |  | REAL | -99.0~99.0
|  |  | InputsCheck.MaxVal_DscgP | 40 | 40041 |  | REAL | -99.0~99.0
| Auxiliary electronic expansion valve |  | EnVaporInj | 30 | 00031 | 1 | BOOL
| Enthalpy increasing valve control mode |  | EEV2_control_mode | 29 | 00030 | 1 | BOOL |  | 0: Inhalation superheat; 1: Exhaust superheat;
| EVI evaporation pressure range | Min | InputsCheck.MinVal_SuctP_EVI | 41 | 40042 |  | REAL | -99.0~99.0
|  | Max | InputsCheck.MaxVal_SuctP_EVI | 42 | 40043 |  | REAL | -99.0~99.0
| Starting conditions for jet enthalpy increase | Compressor speed | VapInjRotSpeedSe | 43 | 40044 |  | REAL | 0.0~999.0
|  | Exhaust superheat setting point | VapInjDischSHSet | 44 | 40045 |  | REAL | 0.0~999.0
|  | Exhaust superheat deviation | VapInjDischSHDiff | 45 | 40046 |  | REAL | 0.0~999.0
| Starting conditions for jet enthalpy increase/cooling | Ambient temp setup | VapInjTExtSetCH | 46 | 40047 |  | REAL | -999.0~999.0
|  | Ambient temp deviation | VapInjTExtDiffCH | 47 | 40048 |  | REAL | -999.0~999.0
| Starting conditions for jet enthalpy increase/heating | Ambient temp setup | VapInjTExtSetHP | 48 | 40049 |  | REAL | -999.0~999.0
|  | Ambient temp deviation | VapInjTExtDiffHP | 49 | 40050 |  | REAL | -999.0~999.0
| Fan shutdown delay | S | DT_FanOff | 213 | 40214 |  | INT | 0~60
| Antifreeze shutdown delay | min | DT_Sysoff_Antif | 214 | 40215 |  | INT | 0~120
| Enable return oil control |  | En_OilRecov | 31 | 00032 | 1 | BOOL
| Minimum demand |  | OilRecovMinReqThrsh | 50 | 40051 |  | REAL | 0.0~99.0
| Minimum speed |  | OilRecovCompMinSpeedThrsh_rps | 51 | 40052 |  | REAL | 0.0~99.0
| Detection delay |  | OilRecovWaitT_min | 52 | 40053 |  | INT | 10~999
| Return oil speed |  | OilRecovFrcCompSpeed_rps | 53 | 40054 |  | REAL | 0.0~200.0
| Oil return time |  | OilRecovFrcSpeedT_min | 54 | 40055 |  | INT | 1~99
| Maximum speed for oil return and defrosting |  | oil_defrost_maxspeed | 55 | 40056 |  | REAL | 0.0~120.0
| Low wind ambient temperature setting point |  | lowfan_amTset | 56 | 40057 |  | REAL | 0.0~999.0
| High air ambient temperature return difference |  | lowfan_amTsetdiff | 57 | 40058 |  | REAL | 0.0~999.0
| cooling mode fan pressure mode | High pressure setting point | set_highpress | 58 | 40059 |  | REAL | 0.0~99.0
|  | Open loop difference | set_highpress_diff | 59 | 40060 |  | REAL | 0.0~99.0
|  | Closing return difference | set_highP_Stop_diff | 60 | 40061 |  | REAL | 0.0~99.0
| heating mode fan pressure mode | Low pressure setting point | set_lowpress | 61 | 40062 |  | REAL | 0.0~99.0
|  | Open loop difference | set_lowpress_diff | 62 | 40063 |  | REAL | 0.0~99.0
|  | Closing return difference | set_lowP_Stop_diff | 63 | 40064 |  | REAL | 0.0~99.0
| address |  | CondenserFan.FAN_address | 64 | 40065 |  | UDINT | 0-999
| Minimum speed of speed regulating fan |  | CondenserFan.FAN_min_rpm | 66 | 40067 |  | REAL | 0.0~9999.0
| Maximum speed of speed regulating fan |  | CondenserFan.FAN_max_rpm | 67 | 40068 |  | REAL | 0.0~9999.0
| Speed control fan activation |  | CondenserFan.en_fan_rpm | 32 | 00033 | 0 | bool
| Alarm deviation |  | CondenserFan.fan_RPM_diff_error | 68 | 40069 |  | real | 0.0~9999.0
| Alarm delay |  | CondenserFan.fan_RPM_error_delay | 69 | 40070 |  | int | 0~999
| Fan communication failure shutdown |  | en_al_fan_offcom | 33 | 00034 | 0 | bool
| Minimum fan speed |  | min_y1_out | 70 | 40071 |  | real | 0.0~100.0
| Maximum fan speed |  | max_y1_out | 71 | 40072 |  | real | 0.0~100.0
| Lowest set point for refrigeration |  | CoolHeatMng.cool_set_min | 72 | 40073 |  | real | -99~100
| Heating highest setting point |  | CoolHeatMng.heat_set_max | 73 | 40074 |  | real | -99~100
| address |  | Protocol.BMS2_Address | 74 | 40075 |  | udint | 1-207
| Enable networking |  | En_NetWork | 34 | 00035 | 0 | bool
| Set Unit Category |  | DevicesRotation_mng.MB_Choise | 35 | 00036 | 0 | bool |  | 0: Slave; 1: Host;
| Set a new password |  | GeneralMng.PwdManuf | 76 | 40077 |  | Uint | 0~9999
| language | [7 empty] | No such variable
（defrost） | Enable defrosting |  | En_DefrostMng | 36 | 00037 | 1 | BOOL
| Defrost switching four-way valve press compensation |  | En_Dfr_PressOffset | 37 | 00038 | 1 | BOOL
| Minimum speed during defrosting switching |  | RevVlvSpeedRps | 77 | 40078 |  | REAL | 30.0~90.0
| Defrosting EEV opening |  | EVD_DfrStep | 78 | 40079 |  | INT | 0-480
| Defrosting exit EEV manual opening |  | EVD_DfrStep2 | 79 | 40080 |  | INT | 0-480
| EEV manual running time |  | EVD_DfrStep2_Time | 80 | 40081 |  | INT | 0~999
| Defrosting compressor speed |  | DfrRunCompPwr | 81 | 40082 |  | REAL | 30.0~oil_defrost_maxspeed（oil_defrost_maxspeed范围0.0~120.0）
| Speed of defrosting main water pump |  | DfrPmpSpeed | 82 | 40083 |  | REAL | 0.0~100.0
| Defrost entry point |  | DefrostCoreMng.DfrStartThrsh | 83 | 40084 |  | REAL | -20.0~30.0
| Defrost end setting point |  | DefrostCoreMng.DfrEndThrsh | 84 | 40085 |  | REAL | 0.0~30.0
| Environmental temperature setting point |  | DefrostCoreMng.AmbTempSetP | 85 | 40086 |  | REAL | -30.0~30.0
| Defrosting environment and coil temperature difference |  | DefrostCoreMng.DfrStartThrsh_DeltaT | 86 | 40087 |  | REAL | 1.0~30.0
| Defrost entry delay |  | DefrostCoreMng.DfrStartDT | 87 | 40088 |  | UINT | 0~90
| Minimize frost time |  | DefrostCoreMng.MinT_DFC | 88 | 40089 |  | UINT | 1-99
| Maximum frost time |  | DefrostCoreMng.MaxT_DFC | 89 | 40090 |  | UINT | 1~99
| Defrosting interval time |  | DefrostCoreMng.IntervalT_DFC | 90 | 40091 |  | UINT | 0-480
| Timed defrosting |  | DefrostCoreMng.Dfr_X_Hrs | 91 | 40092 |  | UINT | 1~999
| Start defrosting |  | DefrostCoreMng.DT_BeforeChgOver_DFC | 92 | 40093 |  | UINT | 0~99
| End defrosting |  | DefrostCoreMng.DT_AfterChgOver_DFC | 93 | 40094 |  | UINT | 0~99
| Drip water fan on time |  | DefrostCoreMng.DripT_DFC | 94 | 40095 |  | UINT | 0-999
| High voltage setting point |  | DefrostCoreMng.Dfr_CondFan_SetP | 95 | 40096 |  | REAL | 0.0~40.0
| Return difference |  | DefrostCoreMng.Dfr_CondFan_Diff | 96 | 40097 |  | REAL | 0.0~10.0
| High voltage setting point |  | Dfr_DscgP_offset | 97 | 40098 |  | REAL | 0.0~40.0
| Low voltage setting point |  | Dfr_SuctP_offset | 98 | 40099 |  | REAL | 0.0~30.0
（EVO OnBoard） | EEV1 MOP protection | Threshold | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.MOP_Thrsh.Val | 99 | 40100 |  | REAL | 0.0~999.0
|  | Integral time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.MOP_Ti.Val | 100 | 40101 |  | REAL | 0.0~999.0
|  | Alarm delay | EVD_Emb_1.Params_EVDEMB_1.EVD.Regulation.MOP_AlrmDT.Val | 101 | 40102 |  | INT | 0~999
| EEV1 | Prop.gain | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Kp.Val | 102 | 40103 |  | REAL | 0.0~999.0
|  | Integr time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Ti.Val | 103 | 40104 |  | REAL | 0.0~3200.0
|  | Deriv time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Td.Val | 104 | 40105 |  | REAL | 0.0~999.0
| Minimum EEVI opening when auxiliary valve is closed |  | EVD_Emb_1.EVD1_MinSteps | 105 | 40106 |  | INT | 0~480
| EEV2 | Prop.gain | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Kp.Val | 106 | 40107 |  | REAL | 0.0~999.0
|  | Integr time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Ti.Val | 107 | 40108 |  | REAL | 0.0~3200.0
|  | Deriv time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Td.Val | 108 | 40109 |  | REAL | 0.0~999.0
| EEV2 MOP protection | Threshold | VD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondThrsh.Val | 109 | 40110 |  | REAL | 0.0~999.0
|  | Integral time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondTi.Val | 110 | 40111 |  | REAL | 0.0~999.0
|  | Alarm delay | EVD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondAlrmDT.Val | 111 | 40112 |  | INT | 0-65536
（user mode） | 10℃＜ambient temp≤14℃ | Main valve superheat | SH_Set1_User[0] | 112 | 40113 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[0] | 113 | 40114 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[0] | 114 | 40115 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[0] | 115 | 40116 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[0] | 116 | 40117 |  | REAL | 0.0~999.0
| 5℃＜ambient temp≤9℃ | Main valve superheat | SH_Set1_User[1] | 117 | 40118 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[1] | 118 | 40119 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[1] | 119 | 40120 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[1] | 120 | 40121 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[1] | 121 | 40122 |  | REAL | 0.0~999.0
| 0℃＜ambient temp≤4℃ | Main valve superheat | SH_Set1_User[2] | 122 | 40123 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[2] | 123 | 40124 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[2] | 124 | 40125 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User2] | 125 | 40126 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[2] | 126 | 40127 |  | REAL | 0.0~999.0
| 一5℃＜ambient temp≤-1℃ | Main valve superheat | SH_Set1_User[3] | 127 | 40128 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[3] | 128 | 40129 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[3] | 129 | 40130 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[3] | 130 | 40131 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[3] | 131 | 40132 |  | REAL | 0.0~999.0
| 一10℃＜ambient temp≤一6℃ | Main valve superheat | SH_Set1_User[4] | 132 | 40133 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[4] | 133 | 40134 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[4] | 134 | 40135 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[4] | 135 | 40136 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[4] | 136 | 40137 |  | REAL | 0.0~999.0
| —15℃＜ambient temp≤一11℃ | Main valve superheat | SH_Set1_User[5] | 137 | 40138 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[5] | 138 | 40139 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[5] | 139 | 40140 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[5] | 140 | 40141 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[5] | 141 | 40142 |  | REAL | 0.0~999.0
| 一20℃＜ambient temp≤一16℃ | Main valve superheat | SH_Set1_User[6] | 142 | 40143 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[6] | 143 | 40144 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[6] | 144 | 40145 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[6] | 145 | 40146 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[6] | 146 | 40147 |  | REAL | 0.0~999.0
| ambient temp≤一21℃ | Main valve superheat | SH_Set1_User[7] | 147 | 40148 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[7] | 148 | 40149 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[7] | 149 | 40150 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[7] | 150 | 40151 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[7] | 151 | 40152 |  | REAL | 0.0~999.0
| 15℃＜ambient temp≤24℃ | Main valve superheat | SH_Set1_User[8] | 152 | 40153 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[8] | 153 | 40154 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[8] | 154 | 40155 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[8] | 155 | 40156 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[8] | 156 | 40157 |  | REAL | 0.0~999.0
| ambient temp＞25℃ | Main valve superheat | SH_Set1_User[9] | 157 | 40158 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[9] | 158 | 40159 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[9] | 159 | 40160 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[9] | 160 | 40161 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[9] | 161 | 40162 |  | REAL | 0.0~999.0
| 33℃＜ambient temp≤37℃ | Main valve superheat | SH_Set1_User[10] | 162 | 40163 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[10] | 163 | 40164 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[10] | 164 | 40165 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[10] | 165 | 40166 |  | REAL | 0.0~999.0
| 30℃＜ambient temp≤32℃ | Main valve superheat | SH_Set1_User[11] | 166 | 40167 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[11] | 167 | 40168 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[11] | 168 | 40169 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[11] | 169 | 40170 |  | REAL | 0.0~999.0
| 26℃＜ambient temp≤29℃ | Main valve superheat | SH_Set1_User[12] | 170 | 40171 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[12] | 171 | 40172 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[12] | 172 | 40173 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[12] | 173 | 40174 |  | REAL | 0.0~999.0
| ambient temp≤25℃ | Main valve superheat | SH_Set1_User[13] | 174 | 40175 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[13] | 175 | 40176 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[13] | 176 | 40177 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[13] | 177 | 40178 |  | REAL | 0.0~999.0
| ambient temp＞38℃ | Main valve superheat | SH_Set1_User[14] | 178 | 40179 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[14] | 179 | 40180 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[14] | 180 | 40181 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[14] | 181 | 40182 |  | REAL | 0.0~999.0
| date | year | GeneralMng.YearIn | 182 | 40183 |  | UINT | 0~99
| date | month | GeneralMng.MonthIn | 183 | 40184 |  | UINT | 0~12
| date | day | GeneralMng.DayIn | 184 | 40185 |  | UINT | 0~31
| time | Hour | GeneralMng.HourIn | 185 | 40186 |  | UINT | 0~23
| time | branch | GeneralMng.MinuteIn | 186 | 40187 |  | UINT | 0~59
| week |  | GeneralMng.DayOfWeek | 187 | 40188 |  | UINT | 1~7
| Enable time zone switch on/off |  | En_SchedOnOff | 38 | 00039 | 0 | bool
| Enable timed change of setting points |  | En_Sch_Setp | 39 | 00040 | 1 | bool
| Enable synchronization |  | En_Date | 43 | 00044 | 0 | bool
| Unit mode | (On/Off) | UnitOn | 0 | 10001 |  | BOOL
B1 | Return water temperature | 0 | CW_InTemp | 188 | 40189 |  | REAL | ℃/℉
B2 | Outlet water temperature | 0 | CW_OutTemp | 189 | 40190 |  | REAL | ℃/℉
B3 | Ambient temp | 0 | AmbTemp | 190 | 40191 |  | REAL | ℃/℉
B4 | Exhaust temperature | 0 | DscgTemp | 191 | 40192 |  | REAL | ℃/℉
B5 | Suction temperature | 0 | SuctTemp | 192 | 40193 |  | REAL | ℃/℉
B6 | High pressure | 0 | DscgP | 193 | 40194 |  | REAL
B7 | Low pressure | 0 | SuctP | 194 | 40195 |  | REAL
B8 | Hot water temperature | 0 | CW_TankTemp | 195 | 40196 |  | REAL | ℃/℉
B9 | Coil temperature | 0 | CondsrCoilTemp | 196 | 40197 |  | REAL | ℃/℉
ID1 | Water flow switch | (On/Off) | InputsCheck.FlwSw_Din | 1 | 10002 |  | BOOL
ID2 | Emergency switch | (On/Off) | InputsCheck.RemoteOnOff_Din | 2 | 10003 |  | BOOL
ID3 | End signal switch | (On/Off) | InputsCheck.Terminal_Switch_Din | 3 | 10004 |  | BOOL
ID5 | Phase sequence protection | (On/Off) | InputsCheck.ProtSeqPh_Din | 4 | 10005 |  | BOOL
D01 | noble character |  | Outputs.DoutVal_1 | 5 | 10006 |  | BOOL
D02 | Low wind |  | Outputs.DoutVal_2 | 6 | 10007 |  | BOOL
D03 | Four way valve |  | Outputs.DoutVal_3 | 7 | 10008 |  | BOOL
D04 | Main engine water pump |  | Outputs.DoutVal_4 | 8 | 10009 |  | BOOL
D05 | Three way valve |  | Outputs.DoutVal_5 | 9 | 10010 |  | BOOL
D06 | Electric heating of crankshaft |  | Outputs.DoutVal_6 | 10 | 10011 |  | BOOL
D07 | Chassis electric heating |  | Outputs.DoutVal_7 | 11 | 10012 |  | BOOL
D09 | Electric heating |  | Outputs.DoutVal_9 | 12 | 10013 |  | BOOL
Y1 | Fan output |  | CondenserFan.y1_out | 197 | 40198 |  | REAL
Y3 | Water pump output |  | Pump_Aout | 198 | 40199 |  | REAL
| Speed regulation fan 1 output |  | CondenserFan.fan1_RPM_OUT_2 | 199 | 40200 |  | INT
| Speed control fan 1 feedback |  | CondenserFan.fan2_RPM_in_2 | 200 | 40201 |  | INT
| Speed regulation fan 2 output |  | CondenserFan.fan2_RPM_OUT_2 | 201 | 40202 |  | INT
| Speed control fan 2 feedback |  | CondenserFan.fan1_RPM_in_2 | 202 | 40203 |  | INT
| Required cap |  | BLDC_Mng.Info_BLDC1.Info_CompRequest | 203 | 40204 |  | REAL
| Actual cap |  | BLDC_Mng.Info_BLDC1.Info_ReqSpeedToPWRP | 204 | 40205 |  | REAL
| Actual speed |  | BLDC_Mng.Info_PWRP1.Info_RotorSpeed_rps | 205 | 40206 |  | REAL
| Evaporation temperature |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH_EvapTemp.Val | 206 | 40207 |  | REAL
| Electronic expansion valve opening |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | 207 | 40208 |  | INT
| Discharge Superheat |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.DscgSH.Val | 208 | 40209 |  | REAL
| Status | Drive status: | BLDC_Mng.Info_BLDC1.Info_HTZone | 209 | 40210 |  | INT |  | 0:ok 1:Controlled 2:limited
| Protection |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.ProtStatus.Val | 210 | 40211 |  | INT |  | 0: none 1：none 2：LowSH 3：lop 4:Mop 5:HiTcond
| Suction SH |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH.Val | 211 | 40212 |  | REAL
| Current operating mode of the unit |  | uniton_mode | 215 | 40216 |  | INT |  | 0: cooling 1: Heating 2: Hot water
| Unit switch on/off |  | OnOffUnitMng.KeybOnOff | 40 | 00041 | 0 | bool |  | 0: Off 1: On
| Current temperature |  | Temp_Target | 216 | 40217 |  | real
| Unit status |  | UnitStatus | 217 | 40218 |  | int | 0-11 | 0: Machine preparation; 1: Unit startup; 2: Alarm shutdown; 3: Network shutdown; 4: Monitoring shutdown; 5: Emergency shutdown; 6: Press the button to shut down; 7: Manual mode; 8: Unit antifreeze; 9: Networking switch; 10: Switching off; 11: High-temperature sterilization
| Water pump switch status |  | Pmp_On | 178 | 10179 |  | BOOL
| Compressor switch status |  | Comp_On | 179 | 10180 |  | BOOL
| Fan switch status |  | FanOn | 180 | 10181 |  | BOOL
| Alarm reset |  | AlrmResByBms | 41 | 00042 | 0 | BOOL
时钟管理 | Start on Monday: hour |  | TimezoneMng.On_Mon_Hour | 218 | 40219 |  | INT | 0-23
| Start on Monday: minutes |  | TimezoneMng.On_Mon_Min | 219 | 40220 |  | INT | 0-59
| On Tuesday: hour |  | TimezoneMng.On_Tue_Hour | 220 | 40221 |  | INT | 0-23
| Starting on Tuesday: minutes |  | TimezoneMng.On_Tue_Min | 221 | 40222 |  | INT | 0-59
| On Wednesday: hour |  | TimezoneMng.On_Wed_Hour | 222 | 40223 |  | INT | 0-23
| Starting on Wednesday: minutes |  | TimezoneMng.On_Wed_Min | 223 | 40224 |  | INT | 0-59
| Start on Thursday: hour |  | TimezoneMng.On_Thu_Hour | 224 | 40225 |  | INT | 0-23
| Start on Thursday: minutes |  | TimezoneMng.On_Thu_Min | 225 | 40226 |  | INT | 0-59
| Start on Friday: hour |  | TimezoneMng.On_Fri_Hour | 226 | 40227 |  | INT | 0-23
| Start on Friday: minutes |  | TimezoneMng.On_Fri_Min | 227 | 40228 |  | INT | 0-59
| Start on Saturday: hour |  | TimezoneMng.On_Sat_Hour | 228 | 40229 |  | INT | 0-23
| Start on Saturday: minutes |  | TimezoneMng.On_Sat_Min | 229 | 40230 |  | INT | 0-59
| Start on Sunday: hour |  | TimezoneMng.On_Sun_Hour | 230 | 40231 |  | INT | 0-23
| Start on Sunday: minutes |  | TimezoneMng.On_Sun_Min | 231 | 40232 |  | INT | 0-59
| Shutdown on Monday: hours |  | TimezoneMng.Off_Mon_Hour | 232 | 40233 |  | INT | 0-23
| Shutdown on Monday: minutes |  | TimezoneMng.Off_Mon_Min | 233 | 40234 |  | INT | 0-59
| Shutdown on Tuesday: hour |  | TimezOffeMng.Off_Tue_Hour | 234 | 40235 |  | INT | 0-23
| Shutdown on Tuesday: minutes |  | TimezOffeMng.Off_Tue_Min | 235 | 40236 |  | INT | 0-59
| Shutdown on Wednesday: hour |  | TimezOffeMng.Off_Wed_Hour | 236 | 40237 |  | INT | 0-23
| Shutdown on Wednesday: minutes |  | TimezOffeMng.Off_Wed_Min | 237 | 40238 |  | INT | 0-59
| Shutdown on Thursday: hour |  | TimezOffeMng.Off_Thu_Hour | 238 | 40239 |  | INT | 0-23
| Shutdown on Thursday: minutes |  | TimezOffeMng.Off_Thu_Min | 239 | 40240 |  | INT | 0-59
| Shutdown on Friday: hour |  | TimezOffeMng.Off_Fri_Hour | 240 | 40241 |  | INT | 0-23
| Shutdown on Friday: minutes |  | TimezOffeMng.Off_Fri_Min | 241 | 40242 |  | INT | 0-59
| Shutdown on Saturday: hour |  | TimezOffeMng.Off_Sat_Hour | 242 | 40243 |  | INT | 0-23
| Shutdown on Saturday: minutes |  | TimezOffeMng.Off_Sat_Min | 243 | 40244 |  | INT | 0-59
| Shutdown on Sunday: hour |  | TimezOffeMng.Off_Sun_Hour | 244 | 40245 |  | INT | 0-23
| Shutdown on Sunday: minutes |  | TimezOffeMng.Off_Sun_Min | 245 | 40246 |  | INT | 0-59
Time Zone 1 Management | Hour |  | TimezoneMng.TempHr1 | 246 | 40247 |  | INT | 0-23
| branch |  | TimezoneMng.TempMin1 | 247 | 40248 |  | INT | 0-59
| refrigeration |  | TimezoneMng.S_Set_Temp1 | 248 | 40249 |  | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp1 | 249 | 40250 |  | REAL | -99.0~99.0
Time Zone 2 Management | Hour |  | TimezoneMng.TempHr2 | 250 | 40251 |  | INT | 0-95
| branch |  | TimezoneMng.TempMin2 | 251 | 40252 |  | INT | 0-131
| refrigeration |  | TimezoneMng.S_Set_Temp2 | 252 | 40253 |  | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp2 | 253 | 40254 |  | REAL | -99.0~99.0
Time Zone 3 Management | Hour |  | TimezoneMng.TempHr3 | 254 | 40255 |  | INT | 0-167
| branch |  | TimezoneMng.TempMin3 | 255 | 40256 |  | INT | 0-203
| refrigeration |  | TimezoneMng.S_Set_Temp3 | 256 | 40257 |  | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp3 | 257 | 40258 |  | REAL | -99.0~99.0
Time Zone 4 Management | Hour |  | TimezoneMng.TempHr4 | 258 | 40259 |  | INT | 0-239
| branch |  | TimezoneMng.TempMin4 | 259 | 40260 |  | INT | 0-275
| refrigeration |  | TimezoneMng.S_Set_Temp4 | 260 | 40261 |  | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp4 | 261 | 40262 |  | REAL | -99.0~99.0
ID4 | Refrigeration linkage | (On/Off) | InputsCheck.CoolSw_Din | 181 | 10182 |  | BOOL
ID6 | Heating linkage | (On/Off) | InputsCheck.HeatSW_Din | 182 | 10183 |  | BOOL
DO8 | End water pump | (On/Off) | Outputs.DoutVal_8 | 183 | 10184 |  | BOOL
| on/off | DI4: Refrigeration linkage | InputsCheck.CoolSw_Logic | 45 | 00046 | 0 | BOOL
|  | DI5: Heating linkage | InputsCheck.HeatSW_Logic | 46 | 00047 | 1 | BOOL
|  | Speed regulating water pump | PumpMng.Enable_Ao_Pump | 47 | 00048 | 0 | BOOL | 0: Disable 1: Enable
|  | EEV2 manual mode | En_EVI_ManMode | 48 | 00049 | 0 | BOOL | 0: Disable 1: Enable
|  | EEV2 manual steps | EVI_ManSteps | 262 | 40263 |  | int | 0-480
|  | Manual low wind | ManDout1 | 49 | 00050 | 0 | BOOL
|  | Manual high wind | ManDout2 | 50 | 00051 | 0 | BOOL
|  | Fan grading windshield mode | fan_mode_bool | 51 | 00052 | 0 | BOOL | 0: Grading position 1: Grading
Fan Economy Mode | Cooling ambient temperature X-axis setting | X1 | X_CH[1] | 276 | 40277 |  | real | -99.9~99.9
|  | X2 | X_CH[2] | 277 | 40278 |  | real | -99.9~99.9
|  | X3 | X_CH[3] | 278 | 40279 |  | real | -99.9~99.9
|  | X4 | X_CH[4] | 279 | 40280 |  | real | -99.9~99.9
| Heating ambient temperature X-axis setting | X1 | X_Hp[1] | 280 | 40281 |  | real | -99.9~99.9
|  | X2 | X_Hp[2] | 281 | 40282 |  | real | -99.9~99.9
|  | X3 | X_Hp[3] | 282 | 40283 |  | real | -99.9~99.9
|  | X4 | X_Hp[4] | 283 | 40284 |  | real | -99.9~99.9
| Hot water ambient temperature X-axis setting | X1 | X_DHW[1] | 284 | 40285 |  | real | -99.9~99.9
|  | X2 | X_DHW[2] | 285 | 40286 |  | real | -99.9~99.9
|  | X3 | X_DHW[3] | 286 | 40287 |  | real | -99.9~99.9
|  | X4 | X_DHW[4] | 287 | 40288 |  | real | -99.9~99.9
| Cooling water temperature Y-axis setting point | Y2 | Y_CH[2] | 288 | 40289 |  | real | -99.9~99.9
|  | Y3 | Y_CH[3] | 289 | 40290 |  | real | -99.9~99.9
|  | Y4 | Y_CH[4] | 290 | 40291 |  | real | -99.9~99.9
| Heating water temperature Y-axis setting point | Y1 | Y_Hp[1] | 291 | 40292 |  | real | -99.9~99.9
|  | Y2 | Y_Hp[2] | 292 | 40293 |  | real | -99.9~99.9
|  | Y3 | Y_Hp[3] | 293 | 40294 |  | real | -99.9~99.9
| Hot water temperature Y-axis setting point | Y1 | Y_DHW[1] | 294 | 40295 |  | real | -99.9~99.9
|  | Y2 | Y_DHW[2] | 295 | 40296 |  | real | -99.9~99.9
|  | Y3 | Y_DHW[3] | 296 | 40297 |  | real | -99.9~99.9
|  | Enable mode switching based on ambient temperature | Enable_AmbTemp_Switch | 52 | 00053 | 1 | bool | 0: Disable 1: Enable
|  | Setting point for environmental temperature switching mode | Amb_switch_SetP | 297 | 40298 |  | real | 10.0~30.0
|  | Loop temperature switching mode return difference | Amb_switch_Offs | 298 | 40299 |  | real | 0.0~20.0
|  | Minimum start interval of water pump | MIN_pumpoffTime | 299 | 40300 |  | int | 1~99min
|  | Correction value of return water temperature | CW_InTemp_Offs | 300 | 40301 |  | real | 0.0~99.0
|  | Correction value of outlet water temperature | CW_OutTemp_Offs | 301 | 40302 |  | real | 0.0~99.0
|  | Ambient temp correction value | AmbTemp_Offs | 302 | 40303 |  | real | 0.0~99.0
|  | Exhaust temperature correction value | DscgTemp_Offs | 303 | 40304 |  | real | 0.0~99.0
|  | Correction value of suction temperature | SuctTemp_Offs | 304 | 40305 |  | real | 0.0~99.0
|  | High pressure correction value | DscgP_Offs | 305 | 40306 |  | real | 0.0~99.0
|  | Low pressure correction value | SuctP_Offs | 306 | 40307 |  | real | 0.0~99.0
|  | Correction value of hot water temperature | Water_Tank_Temp_Offs | 307 | 40308 |  | real | 0.0~99.0
|  | Correction value for coil temperature | CondsrCoilTemp_Offs | 308 | 40309 |  | real | 0.0~99.0
|  | Electronic expansion valve 2 opening | EVD_Emb_1_2.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | 309 | 40310 |  | int | 0-480
|  | High temperature differential load reduction deviation | DeltaTemp_Deload_SetP1 | 310 | 40311 |  | real | 0.0-99.0
|  | High temperature difference frequency limiting deviation | DeltaTemp_Deload_SetP2 | 311 | 40312 |  | real | 0.0-99.0
|  | High temperature difference frequency limiting exit deviation | DeltaTemp_Deload_SetP3 | 312 | 40313 |  | real | 0.0-99.0
|  | Deviation of high water outlet load reduction | OutletHighTemp_Deload_SetP1 | 313 | 40314 |  | real | 0.0-99.0
|  | High water outlet frequency limit deviation | OutletHighTemp_Deload_SetP2 | 314 | 40315 |  | real | 0.0-99.0
|  | Exit deviation of high water outlet frequency limit | OutletHighTemp_Deload_SetP3 | 315 | 40316 |  | real | 0.0-99.0
|  | Deviation of low effluent load reduction | OutletLowTemp_Deload_SetP1 | 316 | 40317 |  | real | 0.0-99.0
|  | Low water outlet frequency limit deviation | OutletLowTemp_Deload_SetP2 | 317 | 40318 |  | real | 0.0-99.0
|  | Low water outlet frequency limit exit deviation | OutletLowTemp_Deload_SetP3 | 318 | 40319 |  | real | 0.0-99.0
|  | Frequency reduction delay | Deloading_delay | 319 | 40320 |  | int | 0-99
|  | Frequency reduction status | Deload_Code | 320 | 40321 |  | int | 0: 1: High temperature differential frequency limit 2: Low water outlet frequency limit 3: High water outlet frequency limit
|  | Frequency reduction interval | Deload_Interval_time | 321 | 40322 |  | int | Unit: seconds
|  | Frequency reduction rate | Deload_rate | 322 | 40323 |  | real
|  | Enable high temperature differential frequency limiting | Enable_DeltaTemp_Limit | 184 | 10185 |  | bool
|  | Enable low water outlet frequency limiting | Enable_LowOutletTemp_Limit | 185 | 10186 |  | bool
|  | Enable high water outlet frequency limiting | Enable_highOutletTemp_Limit | 186 | 10187 |  | bool
|  | Electric heating control | En_AuxHeat | 323 | 40324 |  | INT | 0: Disabled 1: Hot water 2: Floor heating 3: Shared
|  | Antifreeze requirements | Anti_CompReq | 324 | 40325 |  | real
|  | First level antifreeze enable | Enable_Antifreeze_Prevent_first | 53 | 00054 | 1 | bool | 0: Disable 1: Enable
|  | Secondary antifreeze enable | Enable_Antifreeze_Prevent_sec | 54 | 00055 | 0 | bool | 0: Disable 1: Enable
|  | Program version number 1 | GeneralMng.CurrVer.X | 325 | 40326 |  | INT
|  | Program version number 2 | GeneralMng.CurrVer.Y | 326 | 40327 |  | INT
|  | Program version number 3 | GeneralMng.CurrVer.Z | 327 | 40328 |  | INT
|  | Unit Model Code 1 | GeneralMng.UnitType_A | 328 | 40329 |  | INT
|  | Unit Model Code 2 | GeneralMng.UnitType_B | 329 | 40330 |  | INT
|  | Delayed start of the water pump for three minutes during fault standby | Alarm_pumpoff_Time | 330 | 40331 |  | int | min
|  | During normal standby, delay starting the water pump for three minutes | Unit_StandBy_Anti_Delay | 331 | 40332 |  | INT | min
|  | Switch from station to hot water mode and enable hot water demand | Enable_HotWater_mode_switch | 55 | 00056 | 0 | bool | 0: Disable 1: Enable
|  | Input and output frequency converter default value | BLDC_Mng.MiscMng_PWRP1.Mng_WriteDefault | 332 | 40333 |  | int | 0: No 1: Yes
|  | Restore default values | En_WipeMem | 57 | 00058 |  | bool | 0: No 1: Yes
|  | Frequency converter power | BLDC_Mng.Info_PWRP1.Info_MotPwr | 333 | 40334 |  | real
|  | Frequency converter voltage | BLDC_Mng.Info_PWRP1.Info_MotV | 334 | 40335 |  | int
|  | Frequency converter current | BLDC_Mng.Info_PWRP1.Info_MotA | 335 | 40336 |  | real
|  | Refrigeration point compensation | Cool_SetPCompensated_enable | 110 | 00111 |  | bool | 0: Disable 1: Enable
|  | Heating point compensation | Heat_SetPCompensated_enable | 111 | 00112 |  | bool | 0: Disable 1: Enable
|  | Hot water point compensation | W_TankSetPCompensated_enable | 112 | 00113 |  | bool | 0: Disable 1: Enable
|  | Swimming pool switch status | POOL_HeatSw_Din | 113 | 00114 |  | bool | 0: Closed 1: Open
|  | Heating mode enables swimming pool function | En_pool_heat_heat | 114 | 00115 |  | bool | 0: Disable 1: Enable
|  | Hot water mode enables swimming pool function | En_pool_heat_hot | 115 | 00116 |  | bool | 0: Disable 1: Enable
|  | Heating+hot water mode enables swimming pool function | En_pool_heat_heathot | 116 | 00117 |  | bool | 0: Disable 1: Enable
| alarm no. |  | Description | index | modbus |  | data type |  | Description
| AL001 |  | Too many mem writings | 13 | 10014 | 1 | BOOL |  | Frequent writing of storage type variables
| AL002 |  | Retain mem write error | 14 | 10015 | 1 | BOOL |  | Frequent write error alarms for stored variables
| AL003 |  | Inlet probe error | 15 | 10016 | 1 | BOOL |  | Inlet temperature probe faulty or offline
| AL004 |  | Outlet probe error | 16 | 10017 | 1 | BOOL |  | Faulty or offline outlet temperature probe
| AL005 |  | Ambient probe error | 17 | 10018 | 1 | BOOL |  | Ambient temp probe malfunction or offline
| AL006 |  | Condenser coil temp | 18 | 10019 | 1 | BOOL |  | Condensation coil temperature probe faulty or offline
| AL007 |  | Water flow switch | 19 | 10020 | 1 | BOOL |  | Water flow switch alarm
| AL008 |  | Phase sequ.prot.alarm | 20 | 10021 | 1 | BOOL |  | Phase sequence protection switch alarm
| AL009 |  | Unit work hour warning | 21 | 10022 | 1 | BOOL |  | Unit working time warning
| AL010 |  | Pump work hour warning | 22 | 10023 | 1 | BOOL |  | Water pump working time warning
| AL011 |  | Comp.work hour warning | 23 | 10024 | 1 | BOOL |  | Compressor working time warning
| AL012 |  | Cond.fan work hourWarn | 24 | 10025 | 1 | BOOL |  | Working time of condensing fan
| AL013 |  | Low superheat - Vlv.A | 25 | 10026 | 1 | BOOL |  | EEV valve A low superheat alarm
| AL014 |  | Low superheat - Vlv.B | 26 | 10027 | 1 | BOOL |  | EEV valve B low superheat alarm
| AL015 |  | LOP - Vlv.A | 27 | 10028 | 1 | BOOL |  | EEV valve A LOP alarm
| AL016 |  | LOP - Vlv.B | 28 | 10029 | 1 | BOOL |  | EEV valve B LOP alarm
| AL017 |  | MOP - Vlv.A | 29 | 10030 | 1 | BOOL |  | EEV valve A MOP alarm
| AL018 |  | MOP - Vlv.B | 30 | 10031 | 1 | BOOL |  | EEV valve B MOP alarm
| AL019 |  | Motor error - Vlv.A | 31 | 10032 | 1 | BOOL |  | EEV valve A alarm
| AL020 |  | Motor error - Vlv.B | 32 | 10033 | 1 | BOOL |  | EEV valve B alarm
| AL021 |  | Low suct.temp. - Vlv.A | 33 | 10034 | 1 | BOOL |  | EEV valve A low suction temperature alarm
| AL022 |  | Low suct.temp. - Vlv.B | 34 | 10035 | 1 | BOOL |  | EEV valve B low suction temperature alarm
| AL023 |  | High condens.temp.EVD | 35 | 10036 | 1 | BOOL |  | EEV high condensation temperature alarm
| AL024 |  | Probe S1 error EVD | 36 | 10037 | 1 | BOOL |  | EEV S1 probe alarm
| AL025 |  | Probe S2 error EVD | 37 | 10038 | 1 | BOOL |  | EEV S2 probe alarm
| AL026 |  | Probe S3 error EVD | 38 | 10039 | 1 | BOOL |  | EEV S3 probe alarm
| AL027 |  | Probe S4 error EVD | 39 | 10040 | 1 | BOOL |  | EEV S4 probe alarm
| AL028 |  | Battery discharge EVD | 40 | 10041 | 1 | BOOL |  | EEV battery failure
| AL029 |  | EEPROM alarm EVD | 41 | 10042 | 1 | BOOL |  | EEV EEPROM alarm
| AL030 |  | Incomplete closing EVD | 42 | 10043 | 1 | BOOL |  | EEV not fully closed alarm
| AL031 |  | Emergency closing EVD | 43 | 10044 | 1 | BOOL |  | EEV emergency shutdown alarm
| AL032 |  | FW not compatible EVD | 44 | 10045 | 1 | BOOL |  | EEV FW version mismatch
| AL033 |  | Config. error EVD | 45 | 10046 | 1 | BOOL |  | EEV configuration error
| AL034 |  | EVD Driver offline | 46 | 10047 | 1 | BOOL |  | EEV offline alarm
| AL035 |  | BLDC-alarm:High startup DeltaP | 47 | 10048 | 1 | BOOL |  | BLDC - Starting pressure difference too high
| AL036 |  | BLDC-alarm:Compressor shut off | 48 | 10049 | 1 | BOOL |  | BLDC Compressor Off
| AL037 |  | BLDC-alarm:Out of Envelope | 49 | 10050 | 1 | BOOL |  | BLDC - out of operating range
| AL038 |  | BLDC-alarm:Starting fail wait | 50 | 10051 | 1 | BOOL |  | BLDC Compressor Start Failure
| AL039 |  | BLDC-alarm:Starting fail exceeded | 51 | 10052 | 1 | BOOL |  | BLDC Compressor Start Failure
| AL040 |  | BLDC-alarm:Low delta pressure | 52 | 10053 | 1 | BOOL |  | BLDC Low Pressure Differential
| AL041 |  | BLDC-alarm:High discarge gas temp | 53 | 10054 | 1 | BOOL |  | BLDC High Exhaust Temperature
| AL042 |  | Envelope-alarm:High compressor ratio | 54 | 10055 | 1 | BOOL |  | Envelope High voltage ratio
| AL043 |  | Envelope-alarm:High discharge press. | 55 | 10056 | 1 | BOOL |  | Envelope - High exhaust pressure
| AL044 |  | Envelope-alarm:High current | 56 | 10057 | 1 | BOOL |  | Envelope - High current
| AL045 |  | Envelope-alarm:High suction pressure | 57 | 10058 | 1 | BOOL |  | Envelope - High suction pressure
| AL046 |  | Envelope-alarm:Low compressor ratio | 58 | 10059 | 1 | BOOL |  | Envelope - Low voltage ratio
| AL047 |  | Envelope-alarm:Low pressure diff. | 59 | 10060 | 1 | BOOL |  | Envelope - Low pressure difference
| AL048 |  | Envelope-alarm:Low discharge pressure | 60 | 10061 | 1 | BOOL |  | Envelope - Low exhaust pressure
| AL049 |  | Envelope-alarm:Low suction pressure | 61 | 10062 | 1 | BOOL |  | Envelope - Low suction pressure
| AL050 |  | Envelope-alarm:High discharge temp. | 62 | 10063 | 1 | BOOL |  | Envelope - High exhaust temperature
| AL051 |  | Power+ alarm:01-Overcurrent | 63 | 10064 | 1 | BOOL |  | Power+01- Overcurrent
| AL052 |  | Power+ alarm:02-Motor overload | 64 | 10065 | 1 | BOOL |  | Power+02- Motor overload
| AL053 |  | Power+ alarm:03-DCbus overvoltage | 65 | 10066 | 1 | BOOL |  | Power+03-DCbus overvoltage
| AL054 |  | Power+ alarm:04-DCbus undervoltage | 66 | 10067 | 1 | BOOL |  | Power+04-DCbus undervoltage
| AL055 |  | Power+ alarm:05-Drive overtemp. | 67 | 10068 | 1 | BOOL |  | Power+05- Frequency converter overheating
| AL056 |  | Power+ alarm:06-Drive undertemp. | 68 | 10069 | 1 | BOOL |  | Power+06- Inverter under temperature
| AL057 |  | Power+ alarm:07-Overcurrent HW | 69 | 10070 | 1 | BOOL |  | Power+07- Overcurrent HW
| AL058 |  | Power+ alarm:08-Motor overtemp. | 70 | 10071 | 1 | BOOL |  | Power+08- Motor overheating
| AL059 |  | Power+ alarm:09-IGBT module error | 71 | 10072 | 1 | BOOL |  | Power+09-IGBT module failure
| AL060 |  | Power+ alarm:10-CPU error | 72 | 10073 | 1 | BOOL |  | Power+10 CPU failure
| AL061 |  | Power+ alarm:11-Parameter default | 73 | 10074 | 1 | BOOL |  | Power+11- Missing parameter
| AL062 |  | Power+ alarm:12-DCbus ripple | 74 | 10075 | 1 | BOOL |  | Power+12- Bus voltage fluctuation
| AL063 |  | Power+ alarm:13-Data comm. Fault | 75 | 10076 | 1 | BOOL |  | Power+13- Data communication failure
| AL064 |  | Power+ alarm:14-Thermistor fault | 76 | 10077 | 1 | BOOL |  | Power+14- Thermistor fault
| AL065 |  | Power+ alarm:15-Autotuning fault | 77 | 10078 | 1 | BOOL |  | Power+15- automatic adjustment fault
| AL066 |  | Power+ alarm:16-Drive disabled | 78 | 10079 | 1 | BOOL |  | Power+16- frequency converter disabled
| AL067 |  | Power+ alarm:17-Motor phase fault | 79 | 10080 | 1 | BOOL |  | Power+17- Motor phase sequence fault
| AL068 |  | Power+ alarm:18-Internal fan fault | 80 | 10081 | 1 | BOOL |  | Power+18- Fan fault
| AL069 |  | Power+ alarm:19-Speed fault | 81 | 10082 | 1 | BOOL |  | Power+19- Speed fault
| AL070 |  | Power+ alarm:20-PFC module error | 82 | 10083 | 1 | BOOL |  | Power+20-PFC module failure
| AL071 |  | Power+ alarm:21-PFC overvoltage | 83 | 10084 | 1 | BOOL |  | Power+21-PFC overvoltage
| AL072 |  | Power+ alarm:22-PFC undervoltage | 84 | 10085 | 1 | BOOL |  | Power+22-PFC undervoltage
| AL073 |  | Power+ alarm:23-STO DetectionError | 85 | 10086 | 1 | BOOL |  | Power+23-STO error detection
| AL074 |  | Power+ alarm:24-STO DetectionError | 86 | 10087 | 1 | BOOL |  | Power+24-STO error detection
| AL075 |  | Power+ alarm:25-Ground fault | 87 | 10088 | 1 | BOOL |  | Power+25- Ground wire fault
| AL076 |  | Power+ alarm:26-Internal error 1 | 88 | 10089 | 1 | BOOL |  | Power+26-CPU synchronization error 1
| AL077 |  | Power+ alarm:27-Internal error 2 | 89 | 10090 | 1 | BOOL |  | Power+27-CPU synchronization error 2
| AL078 |  | Power+ alarm:28-Drive overload | 90 | 10091 | 1 | BOOL |  | Power+28- Inverter overload
| AL079 |  | Power+ alarm:29-uC safety fault | 91 | 10092 | 1 | BOOL |  | Power+29：uC safety fault
| AL080 |  | Power+ alarm:98-Unexpected restart | 92 | 10093 | 1 | BOOL |  | Power+98：Unexpected restart
| AL081 |  | Power+ alarm:99-Unexpected stop | 93 | 10094 | 1 | BOOL |  | Power+99：Unexpected stop
| AL082 |  | Power+ safety alarm:01-Current meas.fault | 94 | 10095 | 1 | BOOL |  | Power+ safety alarm:01-Current meas.fault
| AL083 |  | Power+ safety alarm:02-Current unbalanced | 95 | 10096 | 1 | BOOL |  | Power+ safety alarm:02-Current unbalanced
| AL084 |  | Power+ safety alarm:03-Over current | 96 | 10097 | 1 | BOOL |  | Power+ safety alarm:03-Over current
| AL085 |  | Power+ safety alarm:04-STO alarm | 97 | 10098 | 1 | BOOL |  | Power+ safety alarm:04-STO alarm
| AL086 |  | Power+ safety alarm:05-STO hardware alarm | 98 | 10099 | 1 | BOOL |  | Power+ safety alarm:05-STO hardware alarm
| AL087 |  | Power+ safety alarm:06-PowerSupply missing | 99 | 10100 | 1 | BOOL |  | Power+ safety alarm:06-PowerSupply missing
| AL088 |  | Power+ safety alarm:07-HW fault cmd.buffer | 100 | 10101 | 1 | BOOL |  | Power+ safety alarm:07-HW fault cmd.buffer
| AL089 |  | Power+ safety alarm:08-HW fault heater c. | 101 | 10102 | 1 | BOOL |  | Power+ safety alarm:08-HW fault heater c.
| AL090 |  | Power+ safety alarm:09-Data comm. Fault | 102 | 10103 | 1 | BOOL |  | Power+ safety alarm:09-Data comm. Fault
| AL091 |  | Power+ safety alarm:10-Compr. stall detect | 103 | 10104 | 1 | BOOL |  | Power+ safety alarm:10-Compr. stall detect
| AL092 |  | Power+ safety alarm:11-DCbus over current | 104 | 10105 | 1 | BOOL |  | Power+ safety alarm:11-DCbus over current
| AL093 |  | Power+ safety alarm:12-HWF DCbus current | 105 | 10106 | 1 | BOOL |  | Power+ safety alarm:12-HWF DCbus current
| AL094 |  | Power+ safety alarm:13-DCbus voltage | 106 | 10107 | 1 | BOOL |  | Power+ safety alarm:13-DCbus voltage
| AL095 |  | Power+ safety alarm:14-HWF DCbus voltage | 107 | 10108 | 1 | BOOL |  | Power+ safety alarm:14-HWF DCbus voltage
| AL096 |  | Power+ safety alarm:15-Input voltage | 108 | 10109 | 1 | BOOL |  | Power+ safety alarm:15-Input voltage
| AL097 |  | Power+ safety alarm:16-HWF input voltage | 109 | 10110 | 1 | BOOL |  | Power+ safety alarm:16-HWF input voltage
| AL098 |  | Power+ safety alarm:17-DCbus power alarm | 110 | 10111 | 1 | BOOL |  | Power+ safety alarm:17-DCbus power alarm
| AL099 |  | Power+ safety alarm:18-HWF power mismatch | 111 | 10112 | 1 | BOOL |  | Power+ safety alarm:18-HWF power mismatch
| AL100 |  | Power+ safety alarm:19-NTC over temp. | 112 | 10113 | 1 | BOOL |  | Power+ safety alarm:19-NTC over temp.
| AL101 |  | Power+ safety alarm:20-NTC under temp. | 113 | 10114 | 1 | BOOL |  | Power+ safety alarm:20-NTC under temp.
| AL102 |  | Power+ safety alarm:21-NTC fault | 114 | 10115 | 1 | BOOL |  | Power+ safety alarm:21-NTC fault
| AL103 |  | Power+ safety alarm:22-HWF sync fault | 115 | 10116 | 1 | BOOL |  | Power+ safety alarm:22-HWF sync fault
| AL104 |  | Power+ safety alarm:23-Invalid parameter | 116 | 10117 | 1 | BOOL |  | Power+ safety alarm:23-Invalid parameter
| AL105 |  | Power+ safety alarm:24-FW fault | 117 | 10118 | 1 | BOOL |  | Power+ safety alarm:24-FW fault
| AL106 |  | Power+ safety alarm:25-HW fault | 118 | 10119 | 1 | BOOL |  | Power+ safety alarm:25-HW fault
| AL107 |  | Power+ safety alarm:26-reseved | 119 | 10120 | 1 | BOOL |  | Power+ safety alarm:26-reseved
| AL108 |  | Power+ safety alarm:27-reseved | 120 | 10121 | 1 | BOOL |  | Power+ safety alarm:27-reseved
| AL109 |  | Power+ safety alarm:28-reseved | 121 | 10122 | 1 | BOOL |  | Power+ safety alarm:28-reseved
| AL110 |  | Power+ safety alarm:29-reseved | 122 | 10123 | 1 | BOOL |  | Power+ safety alarm:29-reseved
| AL111 |  | Power+ safety alarm:30-reseved | 123 | 10124 | 1 | BOOL |  | Power+ safety alarm:30-reseved
| AL112 |  | Power+ safety alarm:31-reseved | 124 | 10125 | 1 | BOOL |  | Power+ safety alarm:31-reseved
| AL113 |  | Power+ safety alarm:32-reseved | 125 | 10126 | 1 | BOOL |  | Power+ safety alarm:32-reseved
| AL114 |  | Power+ alarm:Power+ offline | 126 | 10127 | 1 | BOOL |  | Inverter offline alarm
| AL115 |  | EEV alarm:Low superheat | 127 | 10128 | 1 | BOOL |  | EEV low superheat alarm
| AL116 |  | EEV alarm:LOP | 128 | 10129 | 1 | BOOL |  | EEV LOP alarm
| AL117 |  | EEV alarm:MOP | 129 | 10130 | 1 | BOOL |  | EEV MOP alarm
| AL118 |  | EEV alarm:High condens.temp. | 130 | 10131 | 1 | BOOL |  | EEV high condensation temperature alarm
| AL119 |  | EEV alarm:Low suction temp. | 131 | 10132 | 1 | BOOL |  | EEV low suction temperature alarm
| AL120 |  | EEV alarm:Motor error | 132 | 10133 | 1 | BOOL |  | EEV motor fault
| AL121 |  | EEV alarm:Self Tuning | 133 | 10134 | 1 | BOOL |  | EEV from  PID error
| AL122 |  | EEV alarm:Emergency closing | 134 | 10135 | 1 | BOOL |  | EEV emergency shutdown alarm
| AL123 |  | EEV alarm:Temperature delta | 135 | 10136 | 1 | BOOL |  | EEV temperature difference protection
| AL124 |  | EEV alarm:Pressure delta | 136 | 10137 | 1 | BOOL |  | EEV differential pressure protection
| AL125 |  | EEV alarm:Param.range error | 137 | 10138 | 1 | BOOL |  | EEV range error
| AL126 |  | EEV alarm:ServicePosit% err | 138 | 10139 | 1 | BOOL |  | EEV position signal error
| AL127 |  | EEV alarm:ValveID pin error | 139 | 10140 | 1 | BOOL |  | EEV serial number error
| AL128 |  | Low press alarm | 140 | 10141 | 1 | BOOL |  | Low pressure alarm
| AL129 |  | High press alarm | 141 | 10142 | 1 | BOOL |  | High voltage alarm
| AL130 |  | Disc.temp.probe error | 142 | 10143 | 1 | BOOL |  | Exhaust temperature probe alarm
| AL131 |  | Suct.temp.probe error | 143 | 10144 | 1 | BOOL |  | Suction temperature probe alarm
| AL132 |  | Disc.press.probe error | 144 | 10145 | 1 | BOOL |  | Exhaust pressure probe alarm
| AL133 |  | Suct.press.probe error | 145 | 10146 | 1 | BOOL |  | Suction pressure probe alarm
| AL134 |  | Tank temp.probe error | 146 | 10147 | 1 | BOOL |  | Water tank temperature probe alarm
| AL135 |  | EVI SuctT.probe error | 147 | 10148 | 1 | BOOL |  | EVI suction temperature probe alarm
| AL136 |  | EVI SuctP.probe error | 148 | 10149 | 1 | BOOL |  | EVI suction pressure probe alarm
| AL137 |  | Flow switch alarm | 149 | 10150 | 1 | BOOL |  | Water flow switch alarm
| AL138 |  | High temp. alarm | 150 | 10151 | 1 | BOOL |  | High water outlet temperature alarm
| AL139 |  | Low temp. alarm | 151 | 10152 | 1 | BOOL |  | Low water outlet temperature alarm
| AL140 |  | Temp.delta alarm | 152 | 10153 | 1 | BOOL |  | Inlet and outlet water temperature difference alarm
| AL141 |  | EVI alarm:Param.range error | 153 | 10154 | 1 | BOOL |  | EVI Range Error
| AL142 |  | EVI alarm:Low superheat | 154 | 10155 | 1 | BOOL |  | EVI low superheat alarm
| AL143 |  | EVI alarm:LOP | 155 | 10156 | 1 | BOOL |  | EVI LOP alarm
| AL144 |  | EVI alarm:MOP | 156 | 10157 | 1 | BOOL |  | EVI MOP alarm
| AL145 |  | EVI alarm:High condens.temp. | 157 | 10158 | 1 | BOOL |  | EVI high condensation temperature alarm
| AL146 |  | EVI alarm:Low suction temp. | 158 | 10159 | 1 | BOOL |  | EVI low suction temperature alarm
| AL147 |  | EVI alarm:Motor error | 159 | 10160 | 1 | BOOL |  | EVI motor malfunction
| AL148 |  | EVI alarm:Self Tuning | 160 | 10161 | 1 | BOOL |  | EVI adaptive PID error
| AL149 |  | EVI alarm:Emergency closing | 161 | 10162 | 1 | BOOL |  | EVI emergency shutdown
| AL150 |  | EVI alarm:ServicePosit% err | 162 | 10163 | 1 | BOOL |  | EVI position signal error
| AL151 |  | EVI alarm:ValveID pin error | 163 | 10164 | 1 | BOOL |  | EVI serial number error
| AL152 |  | Supply power error | 164 | 10165 | 1 | BOOL |  | Power frequency fluctuation alarm
| AL153 |  | Fan1 fault | 165 | 10166 | 1 | BOOL |  | Speed control fan 1 malfunction
| AL154 |  | Fan2 fault | 166 | 10167 | 1 | BOOL |  | Speed control fan 2 malfunction
| AL155 |  | Fans Offline | 167 | 10168 | 1 | BOOL |  | Speed control fan communication offline
| AL165 |  | Slave1 Offline | 168 | 10169 | 1 | BOOL |  | 1 # Slave offline
| AL166 |  | Master Offline | 169 | 10170 | 1 | BOOL |  | Host offline
| AL167 |  | Slave2 Offline | 170 | 10171 | 1 | BOOL |  | 2 # slave offline
| AL168 |  | Slave3 Offline | 171 | 10172 | 1 | BOOL |  | 3 # slave offline
| AL169 |  | Slave4 Offline | 172 | 10173 | 1 | BOOL |  | 4 # slave offline
| AL170 |  | Slave5 Offline | 173 | 10174 | 1 | BOOL |  | 5 # slave offline
| AL171 |  | Slave6 Offline | 174 | 10175 | 1 | BOOL |  | 6 # slave offline
| AL172 |  | Slave7 Offline | 175 | 10176 | 1 | BOOL |  | 7 # slave offline
| AL173 |  | Slave8 Offline | 176 | 10177 | 1 | BOOL |  | 8 # slave offline
| AL174 |  | Slave9 Offline | 177 | 10178 | 1 | BOOL |  | 9 # slave offline
2022.01.25增加：
| 融霜标识 |  | Run_DFC | 237 | 10238 | 1 | bool | 融霜显示：0为未融霜，1为正在融霜
| AL176 |  | Al_LowAmbTemp.Active | 239 | 10240 | 1 | bool | ambient temp过低保护报警
| 融霜参数判断环温区间设点1 |  | DefrostCoreMng.Set_AmbTempRange[0] | 478 | 40479 | 1 | real | -99.9~99.9
| 融霜参数判断环温区间设点2 |  | DefrostCoreMng.Set_AmbTempRange[1] | 479 | 40480 | 1 | real | -99.9~99.9
| 环温低于区间设点1的融霜进入温差设点 |  | DefrostCoreMng.Set_DfrStartDeltaTemp[0] | 480 | 40481 | 1 | real | 0.0~99.9
| 环温介于区间设点1和2之间的融霜进入温差设点 |  | DefrostCoreMng.Set_DfrStartDeltaTemp[1] | 481 | 40482 | 1 | real | 0.0~99.9
| 环温低于区间设点1的融霜间隔时间设点 |  | DefrostCoreMng.Set_DfrIntervalTime[0] | 482 | 40483 | 1 | uint | 0~999
| 环温介于区间设点1和2之间的融霜间隔时间设点 |  | DefrostCoreMng.Set_DfrIntervalTime[1] | 483 | 40484 | 1 | uint | 0~999
| 长时间未融霜时间设定：低温运行时间设定（分钟） |  | DefrostCoreMng.DfrStartTime1 | 484 | 40485 | 1 | int | 0~999
| 长时间未融霜时间设定：压缩机运行时间设定（分钟） |  | DefrostCoreMng.DfrStartTime2 | 485 | 40486 | 1 | int | 0~999
| 低环温报警设点 |  | AlarmMng.LowAmbTempSetP | 486 | 40487 | 1 | real | -50.0~10.0
| 低环温报警回差 |  | AlarmMng.LowAmbTempDiff | 487 | 40488 | 1 | real | -20.0~20.0
| 当前设点显示 |  | TempSetP | 488 | 40489 | 1 | real
2022.03.01增加：
| 主阀退出最小开度稳定时间 |  | EVD_Emb_1.ExitMinStepDT | 489 | 40490 | 1 | int | 0~99
| 辅阀开时主阀最小开度 |  | EVD_Emb_1.EVD1_MinSteps_2 | 490 | 40491 | 1 | int | 0~480
2022.03.17增加：
| 低环温高水温补偿：低环温设定值 |  | InputsCheck.AmbTemp_SetP_1 | 339 | 40340 | 1 | real | -35.0~20.0
| 低环温高水温补偿：高水温设定值 |  | InputsCheck.HighWaterTemp_SetP | 340 | 40341 | 1 | real | 35.0~45.0
| 低环温低压补偿:低环温设定值 |  | InputsCheck.AmbTemp_SetP_2 | 341 | 40342 | 1 | real | -35.0~0.0
| 低环温低压补偿:低压补偿值 |  | InputsCheck.SuctP_Compensation_SetP | 342 | 40343 | 1 | real | 0.00~9.99
2022.03.22增加：
| 增焓阀初始开度控制：出水温度设点 |  | EVD_Emb_1_2.StartEEV_OpRatio_CWOutTempSetP | 343 | 40344 | 1 | real | 0.0~99.9
| 增焓阀初始开度控制：低出水温度初始开度设定 |  | EVD_Emb_1_2.StartEEV_OpRatio_SetP_1 | 344 | 40345 | 1 | int | 0~100
| 增焓阀初始开度控制：高出水温度初始开度设定 |  | EVD_Emb_1_2.StartEEV_OpRatio_SetP_2 | 345 | 40346 | 1 | int | 0~100

## Sheet2
AIR TO WATER HEAT PUMP 220V EVI INVERTER |  |  | variable | index | modbus | quantity | data type | range | note
| Electric heating control |  | En_AuxHeat | 0 | 00001 | 1 | bool |  | 0: Day mode; 1: Night mode; 2: Low wind mode; 3: Pressure mode;
| Crankshaft/chassis electric heating control |  | En_Customer_16 | 1 | 00002 | 1 | bool
| Power-off self start |  | OnOffUnitMng.UnitTypAfterPwrOff | 2 | 00003 | 1 | bool
（Manual Control） | Water pump manual |  | En_PmpMan | 3 | 00004 | 1 | BOOL
| Manual speed control fan |  | fan_man_en | 4 | 00005 | 1 | BOOL
| Compressor manual |  | CompMan | 5 | 00006 | 1 | BOOL
| EEV manual |  | EVD_Manual | 6 | 00007 | 1 | BOOL
| Manual four-way valve |  | ManDout3 | 7 | 00008 | 1 | BOOL
| Manual waterway three-way valve |  | ManDout5 | 8 | 00009 | 1 | BOOL
| Manual crankshaft electric heating |  | ManDout6 | 9 | 00010 | 1 | BOOL
| Manual chassis electric heating |  | ManDout7 | 10 | 00011 | 1 | BOOL
| Manual end pump |  | ManDout8 | 11 | 00012 | 1 | BOOL
| Manual electric heating |  | ManDout9 | 12 | 00013 | 1 | BOOL
| Insert frequency converter parameters |  | Insert_POWER | 13 | 00014 | 1 | BOOL
| Enable upper machine monitoring |  | BmsOnOff_En | 15 | 00016 | 1 | BOOL
| normally open/normally closed | ID1: Water flow switch | InputsCheck.FlwSw_Logic | 16 | 00017 | 1 | BOOL
|  | ID2: Emergency switch | InputsCheck.RemoteOnOff_Logic | 17 | 00018 | 1 | BOOL
|  | ID3: End signal switch | InputsCheck.Terminal_Switch_Logic | 18 | 00019 | 1 | BOOL
|  | ID5: power phase | InputsCheck.ProtSeqPh_Logic | 19 | 00020 | 1 | BOOL
|  | DO1: High wind | Outputs.FanHiSpeed_Logic | 20 | 00021 | 1 | BOOL
|  | DO2: Low wind | Outputs.FanHiSpeed_Logic | 21 | 00022 | 1 | BOOL
|  | DO3: Four way valve | FwVlv_On_Logic | 22 | 00023 | 1 | BOOL
|  | DO4: Host water pump | Outputs.Pmp_On_Logic | 23 | 00024 | 1 | BOOL
|  | DO5: Waterway three-way valve | Outputs.ThreeWVlv_Logic | 24 | 00025 | 1 | BOOL
|  | DO6: Electric heating of crankshaft | Outputs.HeatCrack_Logic | 25 | 00026 | 1 | BOOL
|  | DO7: Chassis electric heating | Outputs.Heat_Chassis_Logic | 26 | 00027 | 1 | BOOL
|  | DO8: End pump | Outputs.Terminal_Pump_Logic | 27 | 00028 | 1 | BOOL
|  | DO9: Electric heating | Outputs.AuxHeat_Logic | 28 | 00029 | 1 | BOOL
| Enthalpy increasing valve control mode |  | EEV2_control_mode | 29 | 00030 | 1 | BOOL |  | 0: Inhalation superheat; 1: Exhaust superheat;
| Auxiliary electronic expansion valve |  | EnVaporInj | 30 | 00031 | 1 | BOOL
| Enable return oil control |  | En_OilRecov | 31 | 00032 | 1 | BOOL
| Speed control fan activation |  | CondenserFan.en_fan_rpm | 32 | 00033 | 1 | bool
| Fan communication failure shutdown |  | en_al_fan_offcom | 33 | 00034 | 1 | bool
| Enable networking |  | En_NetWork | 34 | 00035 | 1 | bool
| Set Unit Category |  | DevicesRotation_mng.MB_Choise | 35 | 00036 | 1 | bool |  | 0: Slave; 1: Host;
（defrost） | Enable defrosting |  | En_DefrostMng | 36 | 00037 | 1 | BOOL
| Defrost switching four-way valve press compensation |  | En_Dfr_PressOffset | 37 | 00038 | 1 | BOOL
| Enable time zone switch on/off |  | En_SchedOnOff | 38 | 00039 | 1 | bool
| Enable timed change of setting points |  | En_Sch_Setp | 39 | 00040 | 1 | bool
| Unit switch on/off |  | OnOffUnitMng.KeybOnOff | 40 | 00041 | 1 | bool |  | 0: Off 1: On
| Alarm reset |  | AlrmResByBms | 41 | 00042 | 1 | BOOL
| Unit mode |  | en_three_valve | 42 | 00043 | 1 | BOOL |  | 0: Dual supply 1: Triple supply
| Enable synchronization |  | En_Date | 43 | 00044 | 1 | bool
| on/off | DI4: Refrigeration linkage | InputsCheck.CoolSw_Logic | 45 | 00046 | 1 | BOOL
|  | DI5: Heating linkage | InputsCheck.HeatSW_Logic | 46 | 00047 | 1 | BOOL
|  | Speed regulating water pump | PumpMng.Enable_Ao_Pump | 47 | 00048 | 1 | BOOL | 0: Disable 1: Enable
|  | EEV2 manual mode | En_EVI_ManMode | 48 | 00049 | 1 | BOOL | 0: Disable 1: Enable
|  | Manual low wind | ManDout1 | 49 | 00050 | 1 | BOOL
|  | Manual high wind | ManDout2 | 50 | 00051 | 1 | BOOL
|  | Fan grading windshield mode | fan_mode_bool | 51 | 00052 | 1 | BOOL | 0: Grading position 1: Grading
|  | Enable mode switching based on ambient temperature | Enable_AmbTemp_Switch | 52 | 00053 | 1 | bool | 0: Disable 1: Enable
|  | First level antifreeze enable | Enable_Antifreeze_Prevent_first | 53 | 00054 | 1 | bool | 0: Disable 1: Enable
|  | Secondary antifreeze enable | Enable_Antifreeze_Prevent_sec | 54 | 00055 | 1 | bool | 0: Disable 1: Enable
|  | Switch from station to hot water mode and enable hot water demand | Enable_HotWater_mode_switch | 55 | 00056 | 1 | bool | 0: Disable 1: Enable
|  | Restore default values | En_WipeMem | 57 | 00058 | 1 | bool | 0: No 1: Yes
|  | Refrigeration point compensation | Cool_SetPCompensated_enable | 110 | 00111 | 1 | bool | 0: Disable 1: Enable
|  | Heating point compensation | Heat_SetPCompensated_enable | 111 | 00112 | 1 | bool | 0: Disable 1: Enable
|  | Hot water point compensation | W_TankSetPCompensated_enable | 112 | 00113 | 1 | bool | 0: Disable 1: Enable
|  | Swimming pool switch status | POOL_HeatSw_Din | 113 | 00114 | 1 | bool | 0: Closed 1: Open
|  | Heating mode enables swimming pool function | En_pool_heat_heat | 114 | 00115 | 1 | bool | 0: Disable 1: Enable
|  | Hot water mode enables swimming pool function | En_pool_heat_hot | 115 | 00116 | 1 | bool | 0: Disable 1: Enable
|  | Heating+hot water mode enables swimming pool function | En_pool_heat_heathot | 116 | 00117 | 1 | bool | 0: Disable 1: Enable
| Unit mode | (On/Off) | UnitOn | 0 | 10001 | 1 | BOOL
ID1 | Water flow switch | (On/Off) | InputsCheck.FlwSw_Din | 1 | 10002 | 1 | BOOL
ID2 | Emergency switch | (On/Off) | InputsCheck.RemoteOnOff_Din | 2 | 10003 | 1 | BOOL
ID3 | End signal switch | (On/Off) | InputsCheck.Terminal_Switch_Din | 3 | 10004 | 1 | BOOL
ID5 | Phase sequence protection | (On/Off) | InputsCheck.ProtSeqPh_Din | 4 | 10005 | 1 | BOOL
D01 | noble character |  | Outputs.DoutVal_1 | 5 | 10006 | 1 | BOOL
D02 | Low wind |  | Outputs.DoutVal_2 | 6 | 10007 | 1 | BOOL
D03 | Four way valve |  | Outputs.DoutVal_3 | 7 | 10008 | 1 | BOOL
D04 | Main engine water pump |  | Outputs.DoutVal_4 | 8 | 10009 | 1 | BOOL
D05 | Three way valve |  | Outputs.DoutVal_5 | 9 | 10010 | 1 | BOOL
D06 | Electric heating of crankshaft |  | Outputs.DoutVal_6 | 10 | 10011 | 1 | BOOL
D07 | Chassis electric heating |  | Outputs.DoutVal_7 | 11 | 10012 | 1 | BOOL
D09 | Electric heating |  | Outputs.DoutVal_9 | 12 | 10013 | 1 | BOOL
| Water pump switch status |  | Pmp_On | 178 | 10179 | 1 | BOOL
| Compressor switch status |  | Comp_On | 179 | 10180 | 1 | BOOL
| Fan switch status |  | FanOn | 180 | 10181 | 1 | BOOL
ID4 | Refrigeration linkage | (On/Off) | InputsCheck.CoolSw_Din | 181 | 10182 | 1 | BOOL
ID6 | Heating linkage | (On/Off) | InputsCheck.HeatSW_Din | 182 | 10183 | 1 | BOOL
DO8 | End water pump | (On/Off) | Outputs.DoutVal_8 | 183 | 10184 | 1 | BOOL
|  | Enable high temperature differential frequency limiting | Enable_DeltaTemp_Limit | 184 | 10185 | 1 | bool
|  | Enable low water outlet frequency limiting | Enable_LowOutletTemp_Limit | 185 | 10186 | 1 | bool
|  | Enable high water outlet frequency limiting | Enable_highOutletTemp_Limit | 186 | 10187 | 1 | bool
User parameter settings（User mask） | Working mode |  | CoolHeat_Mode | 0 | 40001 | 1 | int | 0~5 | 0: Cooling mode; 1: Heating mode; 2: Hot water mode; 3: Hot water+refrigeration; 4: Hot water+heating; 5: Swimming pool
| Heating setting point |  | HeatSetP | 1 | 40002 | 1 | REAL | 10.0~CoolHeatMng.heat_set_max默认55 | Set value ℃
| Refrigeration setting point |  | CoolSetP | 2 | 40003 | 1 | REAL | CoolHeatMng.cool_set_min默认12~40.0 | Set value ℃
| Hot water point setting |  | W_TankSetP | 3 | 40004 | 1 | REAL | 10.0~CoolHeatMng.heat_set_max默认55 | Set value ℃
| Hot water return difference |  | hotwater_start_diff | 4 | 40005 | 1 | REAL | 1.0~15.0
| Hot water constant temperature shutdown |  | hotwater_stop_diff | 5 | 40006 | 1 | REAL | 0.0~5.0
| Cooling and heating return difference |  | Temp_Diff | 6 | 40007 | 1 | REAL | 1.0~15.0
| Refrigeration heating constant temperature shutdown |  | Stop_TemP_Diff | 7 | 40008 | 1 | REAL | 0.0~5.0
| deviation |  | Kp | 8 | 40009 | 1 | REAL | 1.0~999.0
| Integral time |  | Ti | 9 | 40010 | 1 | UINT | 0-9999
| Differential time |  | Td | 10 | 40011 | 1 | UINT | 0-9999
| Main engine water pump |  | PmpMode | 11 | 40012 | 1 | int | 0~1 | 0: on; 1: Based on demand;
| Fan mode |  | FanMode_Sel | 12 | 40013 | 1 | int | 0~3
| Electric heating start delay |  | DT_AuxComp | 13 | 40014 | 1 | UINT | 0-999
| Electric heating start temperature |  | AuxHeatSetP_Exterior | 14 | 40015 | 1 | real | -30.0~20.0
| Main water pump control | Speed control inlet and outlet water temperature difference | PmpDeltaTempSetP | 15 | 40016 | 1 | real | 2.0~15.0
Configure compressor parameters（ BLDC COMPRESSOR） | Low pressure alarm delay | start delay | StartUpDT_SuctLowP | 16 | 40017 | 1 | int | 0~999
|  | Operation delay | DT_SuctLowPrun | 17 | 40018 | 1 | int | 0~999
| Speed management | Start-up forced speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_StartUpSpeed | 18 | 40019 | 1 | REAL | 20.0~120.0
|  | Max speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_MaxSpeedRpsCustom | 19 | 40020 | 1 | REAL | 0.0~999.0
|  | Min speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_MinSpeedRpsCustom | 20 | 40021 | 1 | REAL | 0.0~99.0
| Comp BLDC | Out of envelope alarm timeout | BLDC_Mng.CfgEnvCtrl_BLDC1.CstmEnv_EnvOutMaxT | 21 | 40022 | 1 | INT | 0-32000
|  | Low pressure diff alarm timeout | BLDC_Mng.CfgEnvCtrl_BLDC1.CstmEnv_LowDeltaPAlrmDelay | 22 | 40023 | 1 | INT | 0-32000
| Manual requirements |  | PmpMan_Aout | 23 | 40024 | 1 | REAL | 0.0~100.0
| Manual requirements |  | fan_man_out | 24 | 40025 | 1 | REAL | 0.0~100.0
| Manual requirements |  | ManBLDCPwrReq | 25 | 40026 | 1 | REAL | 0.0~100.0
| Manual Steps |  | EVD_Manual_Step | 26 | 40027 | 1 | INT | 0-480
（OTHER PARAMETERS） | Temperature mode |  | Temp_Target_Select | 27 | 40028 | 1 | INT | 0~1 | 0: Water inlet temperature; 1: Outlet water temperature;
| Protection value of inlet and outlet water temperature difference |  | DeltaTempSetP | 28 | 40029 | 1 | REAL | 2.0~15.0
| Low water temperature protection value |  | OutLowTempSetP | 29 | 40030 | 1 | REAL | -99.0~99.0
| High water temperature protection value |  | OutHiTempSetP | 30 | 40031 | 1 | REAL | -99.0~99.0
| Delay after startup | S | threevlv_delayon | 31 | 40032 | 1 | INT | 0-999
| Delay before stopping | S | threevlv_delayoff | 32 | 40033 | 1 | INT | 0-999
| Starting speed of three-way valve |  | PmpSpeedStart | 33 | 40034 | 1 | REAL | 0.0~100.0
| Three way valve start delay | min | DT_PmpStart | 34 | 40035 | 1 | INT | 0-999
| Maximum speed |  | PmpMaxSpeed | 35 | 40036 | 1 | REAL | 0.0~100.0
| Minimum speed |  | PmpMinSpeed | 36 | 40037 | 1 | REAL | 0.0~100.0
| Probe range | Main valve suction pressure range | nputsCheck.MinVal_SuctP | 37 | 40038 | 1 | REAL | -99.0~99.0
|  |  | InputsCheck.MaxVal_SuctP | 38 | 40039 | 1 | REAL | -99.0~99.0
|  | Main valve exhaust pressure range | InputsCheck.MinVal_DscgP | 39 | 40040 | 1 | REAL | -99.0~99.0
|  |  | InputsCheck.MaxVal_DscgP | 40 | 40041 | 1 | REAL | -99.0~99.0
| EVI evaporation pressure range | Min | InputsCheck.MinVal_SuctP_EVI | 41 | 40042 | 1 | REAL | -99.0~99.0
|  | Max | InputsCheck.MaxVal_SuctP_EVI | 42 | 40043 | 1 | REAL | -99.0~99.0
| Starting conditions for jet enthalpy increase | Compressor speed | VapInjRotSpeedSe | 43 | 40044 | 1 | REAL | 0.0~999.0
|  | Exhaust superheat setting point | VapInjDischSHSet | 44 | 40045 | 1 | REAL | 0.0~999.0
|  | Exhaust superheat deviation | VapInjDischSHDiff | 45 | 40046 | 1 | REAL | 0.0~999.0
| Starting conditions for jet enthalpy increase/cooling | Ambient temp setup | VapInjTExtSetCH | 46 | 40047 | 1 | REAL | -999.0~999.0
|  | Ambient temp deviation | VapInjTExtDiffCH | 47 | 40048 | 1 | REAL | -999.0~999.0
| Starting conditions for jet enthalpy increase/heating | Ambient temp setup | VapInjTExtSetHP | 48 | 40049 | 1 | REAL | -999.0~999.0
|  | Ambient temp deviation | VapInjTExtDiffHP | 49 | 40050 | 1 | REAL | -999.0~999.0
| Minimum demand |  | OilRecovMinReqThrsh | 50 | 40051 | 1 | REAL | 0.0~99.0
| Minimum speed |  | OilRecovCompMinSpeedThrsh_rps | 51 | 40052 | 1 | REAL | 0.0~99.0
| Detection delay |  | OilRecovWaitT_min | 52 | 40053 | 1 | INT | 10~999
| Return oil speed |  | OilRecovFrcCompSpeed_rps | 53 | 40054 | 1 | REAL | 0.0~200.0
| Oil return time |  | OilRecovFrcSpeedT_min | 54 | 40055 | 1 | INT | 1~99
| Maximum speed for oil return and defrosting |  | oil_defrost_maxspeed | 55 | 40056 | 1 | REAL | 0.0~120.0
| Low wind ambient temperature setting point |  | lowfan_amTset | 56 | 40057 | 1 | REAL | 0.0~999.0
| High air ambient temperature return difference |  | lowfan_amTsetdiff | 57 | 40058 | 1 | REAL | 0.0~999.0
| cooling mode fan pressure mode | High pressure setting point | set_highpress | 58 | 40059 | 1 | REAL | 0.0~99.0
|  | Open loop difference | set_highpress_diff | 59 | 40060 | 1 | REAL | 0.0~99.0
|  | Closing return difference | set_highP_Stop_diff | 60 | 40061 | 1 | REAL | 0.0~99.0
| heating mode fan pressure mode | Low pressure setting point | set_lowpress | 61 | 40062 | 1 | REAL | 0.0~99.0
|  | Open loop difference | set_lowpress_diff | 62 | 40063 | 1 | REAL | 0.0~99.0
|  | Closing return difference | set_lowP_Stop_diff | 63 | 40064 | 1 | REAL | 0.0~99.0
| address |  | CondenserFan.FAN_address | 64 | 40065 | 2 | UDINT | 0-999
| Minimum speed of speed regulating fan |  | CondenserFan.FAN_min_rpm | 66 | 40067 | 1 | REAL | 0.0~9999.0
| Maximum speed of speed regulating fan |  | CondenserFan.FAN_max_rpm | 67 | 40068 | 1 | REAL | 0.0~9999.0
| Alarm deviation |  | CondenserFan.fan_RPM_diff_error | 68 | 40069 | 1 | real | 0.0~9999.0
| Alarm delay |  | CondenserFan.fan_RPM_error_delay | 69 | 40070 | 1 | int | 0~999
| Minimum fan speed |  | min_y1_out | 70 | 40071 | 1 | real | 0.0~100.0
| Maximum fan speed |  | max_y1_out | 71 | 40072 | 1 | real | 0.0~100.0
| Lowest set point for refrigeration |  | CoolHeatMng.cool_set_min | 72 | 40073 | 1 | real | -99~100
| Heating highest setting point |  | CoolHeatMng.heat_set_max | 73 | 40074 | 1 | real | -99~100
| address |  | Protocol.BMS2_Address | 74 | 40075 | 2 | udint | 1-207
| Set a new password |  | GeneralMng.PwdManuf | 76 | 40077 | 1 | Uint | 0~9999
| Minimum speed during defrosting switching |  | RevVlvSpeedRps | 77 | 40078 | 1 | REAL | 30.0~90.0
| Defrosting EEV opening |  | EVD_DfrStep | 78 | 40079 | 1 | INT | 0-480
| Defrosting exit EEV manual opening |  | EVD_DfrStep2 | 79 | 40080 | 1 | INT | 0-480
| EEV manual running time |  | EVD_DfrStep2_Time | 80 | 40081 | 1 | INT | 0~999
| Defrosting compressor speed |  | DfrRunCompPwr | 81 | 40082 | 1 | REAL | 30.0~oil_defrost_maxspeed（oil_defrost_maxspeed范围0.0~120.0）
| Speed of defrosting main water pump |  | DfrPmpSpeed | 82 | 40083 | 1 | REAL | 0.0~100.0
| Defrost entry point |  | DefrostCoreMng.DfrStartThrsh | 83 | 40084 | 1 | REAL | -20.0~30.0
| Defrost end setting point |  | DefrostCoreMng.DfrEndThrsh | 84 | 40085 | 1 | REAL | 0.0~30.0
| Environmental temperature setting point |  | DefrostCoreMng.AmbTempSetP | 85 | 40086 | 1 | REAL | -30.0~30.0
| Defrosting environment and coil temperature difference |  | DefrostCoreMng.DfrStartThrsh_DeltaT | 86 | 40087 | 1 | REAL | 1.0~30.0
| Defrost entry delay |  | DefrostCoreMng.DfrStartDT | 87 | 40088 | 1 | UINT | 0~90
| Minimize frost time |  | DefrostCoreMng.MinT_DFC | 88 | 40089 | 1 | UINT | 1-99
| Maximum frost time |  | DefrostCoreMng.MaxT_DFC | 89 | 40090 | 1 | UINT | 1~99
| Defrosting interval time |  | DefrostCoreMng.IntervalT_DFC | 90 | 40091 | 1 | UINT | 0-480
| Timed defrosting |  | DefrostCoreMng.Dfr_X_Hrs | 91 | 40092 | 1 | UINT | 1~999
| Start defrosting |  | DefrostCoreMng.DT_BeforeChgOver_DFC | 92 | 40093 | 1 | UINT | 0~99
| End defrosting |  | DefrostCoreMng.DT_AfterChgOver_DFC | 93 | 40094 | 1 | UINT | 0~99
| Drip water fan on time |  | DefrostCoreMng.DripT_DFC | 94 | 40095 | 1 | UINT | 0-999
| High voltage setting point |  | DefrostCoreMng.Dfr_CondFan_SetP | 95 | 40096 | 1 | REAL | 0.0~40.0
| Return difference |  | DefrostCoreMng.Dfr_CondFan_Diff | 96 | 40097 | 1 | REAL | 0.0~10.0
| High voltage setting point |  | Dfr_DscgP_offset | 97 | 40098 | 1 | REAL | 0.0~40.0
| Low voltage setting point |  | Dfr_SuctP_offset | 98 | 40099 | 1 | REAL | 0.0~30.0
（EVO OnBoard） | EEV1 MOP protection | Threshold | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.MOP_Thrsh.Val | 99 | 40100 | 1 | REAL | 0.0~999.0
|  | Integral time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.MOP_Ti.Val | 100 | 40101 | 1 | REAL | 0.0~999.0
|  | Alarm delay | EVD_Emb_1.Params_EVDEMB_1.EVD.Regulation.MOP_AlrmDT.Val | 101 | 40102 | 1 | INT | 0~999
| EEV1 | Prop.gain | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Kp.Val | 102 | 40103 | 1 | REAL | 0.0~999.0
|  | Integr time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Ti.Val | 103 | 40104 | 1 | REAL | 0.0~3200.0
|  | Deriv time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Td.Val | 104 | 40105 | 1 | REAL | 0.0~999.0
| Minimum EEVI opening when auxiliary valve is closed |  | EVD_Emb_1.EVD1_MinSteps | 105 | 40106 | 1 | INT | 0~480
| EEV2 | Prop.gain | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Kp.Val | 106 | 40107 | 1 | REAL | 0.0~999.0
|  | Integr time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Ti.Val | 107 | 40108 | 1 | REAL | 0.0~3200.0
|  | Deriv time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Td.Val | 108 | 40109 | 1 | REAL | 0.0~999.0
| EEV2 MOP protection | Threshold | VD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondThrsh.Val | 109 | 40110 | 1 | REAL | 0.0~999.0
|  | Integral time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondTi.Val | 110 | 40111 | 1 | REAL | 0.0~999.0
|  | Alarm delay | EVD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondAlrmDT.Val | 111 | 40112 | 1 | INT | 0-65536
（user mode） | 10℃＜ambient temp≤14℃ | Main valve superheat | SH_Set1_User[0] | 112 | 40113 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[0] | 113 | 40114 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[0] | 114 | 40115 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[0] | 115 | 40116 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[0] | 116 | 40117 | 1 | REAL | 0.0~999.0
| 5℃＜ambient temp≤9℃ | Main valve superheat | SH_Set1_User[1] | 117 | 40118 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[1] | 118 | 40119 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[1] | 119 | 40120 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[1] | 120 | 40121 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[1] | 121 | 40122 | 1 | REAL | 0.0~999.0
| 0℃＜ambient temp≤4℃ | Main valve superheat | SH_Set1_User[2] | 122 | 40123 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[2] | 123 | 40124 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[2] | 124 | 40125 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User2] | 125 | 40126 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[2] | 126 | 40127 | 1 | REAL | 0.0~999.0
| 一5℃＜ambient temp≤-1℃ | Main valve superheat | SH_Set1_User[3] | 127 | 40128 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[3] | 128 | 40129 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[3] | 129 | 40130 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[3] | 130 | 40131 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[3] | 131 | 40132 | 1 | REAL | 0.0~999.0
| 一10℃＜ambient temp≤一6℃ | Main valve superheat | SH_Set1_User[4] | 132 | 40133 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[4] | 133 | 40134 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[4] | 134 | 40135 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[4] | 135 | 40136 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[4] | 136 | 40137 | 1 | REAL | 0.0~999.0
| —15℃＜ambient temp≤一11℃ | Main valve superheat | SH_Set1_User[5] | 137 | 40138 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[5] | 138 | 40139 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[5] | 139 | 40140 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[5] | 140 | 40141 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[5] | 141 | 40142 | 1 | REAL | 0.0~999.0
| 一20℃＜ambient temp≤一16℃ | Main valve superheat | SH_Set1_User[6] | 142 | 40143 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[6] | 143 | 40144 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[6] | 144 | 40145 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[6] | 145 | 40146 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[6] | 146 | 40147 | 1 | REAL | 0.0~999.0
| ambient temp≤一21℃ | Main valve superheat | SH_Set1_User[7] | 147 | 40148 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[7] | 148 | 40149 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[7] | 149 | 40150 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[7] | 150 | 40151 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[7] | 151 | 40152 | 1 | REAL | 0.0~999.0
| 15℃＜ambient temp≤24℃ | Main valve superheat | SH_Set1_User[8] | 152 | 40153 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[8] | 153 | 40154 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[8] | 154 | 40155 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[8] | 155 | 40156 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[8] | 156 | 40157 | 1 | REAL | 0.0~999.0
| ambient temp＞25℃ | Main valve superheat | SH_Set1_User[9] | 157 | 40158 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[9] | 158 | 40159 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[9] | 159 | 40160 | 1 | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[9] | 160 | 40161 | 1 | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[9] | 161 | 40162 | 1 | REAL | 0.0~999.0
| 33℃＜ambient temp≤37℃ | Main valve superheat | SH_Set1_User[10] | 162 | 40163 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[10] | 163 | 40164 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[10] | 164 | 40165 | 1 | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[10] | 165 | 40166 | 1 | REAL | 0.0~999.0
| 30℃＜ambient temp≤32℃ | Main valve superheat | SH_Set1_User[11] | 166 | 40167 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[11] | 167 | 40168 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[11] | 168 | 40169 | 1 | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[11] | 169 | 40170 | 1 | REAL | 0.0~999.0
| 26℃＜ambient temp≤29℃ | Main valve superheat | SH_Set1_User[12] | 170 | 40171 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[12] | 171 | 40172 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[12] | 172 | 40173 | 1 | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[12] | 173 | 40174 | 1 | REAL | 0.0~999.0
| ambient temp≤25℃ | Main valve superheat | SH_Set1_User[13] | 174 | 40175 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[13] | 175 | 40176 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[13] | 176 | 40177 | 1 | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[13] | 177 | 40178 | 1 | REAL | 0.0~999.0
| ambient temp＞38℃ | Main valve superheat | SH_Set1_User[14] | 178 | 40179 | 1 | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[14] | 179 | 40180 | 1 | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[14] | 180 | 40181 | 1 | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[14] | 181 | 40182 | 1 | REAL | 0.0~999.0
| date | year | GeneralMng.YearIn | 182 | 40183 | 1 | UINT | 0~99
| date | month | GeneralMng.MonthIn | 183 | 40184 | 1 | UINT | 0~12
| date | day | GeneralMng.DayIn | 184 | 40185 | 1 | UINT | 0~31
| time | Hour | GeneralMng.HourIn | 185 | 40186 | 1 | UINT | 0~23
| time | branch | GeneralMng.MinuteIn | 186 | 40187 | 1 | UINT | 0~59
| week |  | GeneralMng.DayOfWeek | 187 | 40188 | 1 | UINT | 1~7
B1 | Return water temperature | 0 | CW_InTemp | 188 | 40189 | 1 | REAL | ℃/℉
B2 | Outlet water temperature | 0 | CW_OutTemp | 189 | 40190 | 1 | REAL | ℃/℉
B3 | Ambient temp | 0 | AmbTemp | 190 | 40191 | 1 | REAL | ℃/℉
B4 | Exhaust temperature | 0 | DscgTemp | 191 | 40192 | 1 | REAL | ℃/℉
B5 | Suction temperature | 0 | SuctTemp | 192 | 40193 | 1 | REAL | ℃/℉
B6 | High pressure | 0 | DscgP | 193 | 40194 | 1 | REAL
B7 | Low pressure | 0 | SuctP | 194 | 40195 | 1 | REAL
B8 | Hot water temperature | 0 | CW_TankTemp | 195 | 40196 | 1 | REAL | ℃/℉
B9 | Coil temperature | 0 | CondsrCoilTemp | 196 | 40197 | 1 | REAL | ℃/℉
Y1 | Fan output |  | CondenserFan.y1_out | 197 | 40198 | 1 | REAL
Y3 | Water pump output |  | Pump_Aout | 198 | 40199 | 1 | REAL
| Speed regulation fan 1 output |  | CondenserFan.fan1_RPM_OUT_2 | 199 | 40200 | 1 | INT
| Speed control fan 1 feedback |  | CondenserFan.fan2_RPM_in_2 | 200 | 40201 | 1 | INT
| Speed regulation fan 2 output |  | CondenserFan.fan2_RPM_OUT_2 | 201 | 40202 | 1 | INT
| Speed control fan 2 feedback |  | CondenserFan.fan1_RPM_in_2 | 202 | 40203 | 1 | INT
| Required cap |  | BLDC_Mng.Info_BLDC1.Info_CompRequest | 203 | 40204 | 1 | REAL
| Actual cap |  | BLDC_Mng.Info_BLDC1.Info_ReqSpeedToPWRP | 204 | 40205 | 1 | REAL
| Actual speed |  | BLDC_Mng.Info_PWRP1.Info_RotorSpeed_rps | 205 | 40206 | 1 | REAL
| Evaporation temperature |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH_EvapTemp.Val | 206 | 40207 | 1 | REAL
| Electronic expansion valve opening |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | 207 | 40208 | 1 | INT
| Discharge Superheat |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.DscgSH.Val | 208 | 40209 | 1 | REAL
| Status | Drive status: | BLDC_Mng.Info_BLDC1.Info_HTZone | 209 | 40210 | 1 | INT |  | 0:ok 1:Controlled 2:limited
| Protection |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.ProtStatus.Val | 210 | 40211 | 1 | INT |  | 0: none 1：none 2：LowSH 3：lop 4:Mop 5:HiTcond
| Suction SH |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH.Val | 211 | 40212 | 1 | REAL
| Fan shutdown delay | S | DT_FanOff | 213 | 40214 | 1 | INT | 0~60
| Antifreeze shutdown delay | min | DT_Sysoff_Antif | 214 | 40215 | 1 | INT | 0~120
| Current operating mode of the unit |  | uniton_mode | 215 | 40216 | 1 | INT |  | 0: cooling 1: Heating 2: Hot water
| Current temperature |  | Temp_Target | 216 | 40217 | 1 | real
| Unit status |  | UnitStatus | 217 | 40218 | 1 | int | 0-11 | 0: Machine preparation; 1: Unit startup; 2: Alarm shutdown; 3: Network shutdown; 4: Monitoring shutdown; 5: Emergency shutdown; 6: Press the button to shut down; 7: Manual mode; 8: Unit antifreeze; 9: Networking switch; 10: Switching off; 11: High-temperature sterilization
时钟管理 | Start on Monday: hour |  | TimezoneMng.On_Mon_Hour | 218 | 40219 | 1 | INT | 0-23
| Start on Monday: minutes |  | TimezoneMng.On_Mon_Min | 219 | 40220 | 1 | INT | 0-59
| On Tuesday: hour |  | TimezoneMng.On_Tue_Hour | 220 | 40221 | 1 | INT | 0-23
| Starting on Tuesday: minutes |  | TimezoneMng.On_Tue_Min | 221 | 40222 | 1 | INT | 0-59
| On Wednesday: hour |  | TimezoneMng.On_Wed_Hour | 222 | 40223 | 1 | INT | 0-23
| Starting on Wednesday: minutes |  | TimezoneMng.On_Wed_Min | 223 | 40224 | 1 | INT | 0-59
| Start on Thursday: hour |  | TimezoneMng.On_Thu_Hour | 224 | 40225 | 1 | INT | 0-23
| Start on Thursday: minutes |  | TimezoneMng.On_Thu_Min | 225 | 40226 | 1 | INT | 0-59
| Start on Friday: hour |  | TimezoneMng.On_Fri_Hour | 226 | 40227 | 1 | INT | 0-23
| Start on Friday: minutes |  | TimezoneMng.On_Fri_Min | 227 | 40228 | 1 | INT | 0-59
| Start on Saturday: hour |  | TimezoneMng.On_Sat_Hour | 228 | 40229 | 1 | INT | 0-23
| Start on Saturday: minutes |  | TimezoneMng.On_Sat_Min | 229 | 40230 | 1 | INT | 0-59
| Start on Sunday: hour |  | TimezoneMng.On_Sun_Hour | 230 | 40231 | 1 | INT | 0-23
| Start on Sunday: minutes |  | TimezoneMng.On_Sun_Min | 231 | 40232 | 1 | INT | 0-59
| Shutdown on Monday: hours |  | TimezoneMng.Off_Mon_Hour | 232 | 40233 | 1 | INT | 0-23
| Shutdown on Monday: minutes |  | TimezoneMng.Off_Mon_Min | 233 | 40234 | 1 | INT | 0-59
| Shutdown on Tuesday: hour |  | TimezOffeMng.Off_Tue_Hour | 234 | 40235 | 1 | INT | 0-23
| Shutdown on Tuesday: minutes |  | TimezOffeMng.Off_Tue_Min | 235 | 40236 | 1 | INT | 0-59
| Shutdown on Wednesday: hour |  | TimezOffeMng.Off_Wed_Hour | 236 | 40237 | 1 | INT | 0-23
| Shutdown on Wednesday: minutes |  | TimezOffeMng.Off_Wed_Min | 237 | 40238 | 1 | INT | 0-59
| Shutdown on Thursday: hour |  | TimezOffeMng.Off_Thu_Hour | 238 | 40239 | 1 | INT | 0-23
| Shutdown on Thursday: minutes |  | TimezOffeMng.Off_Thu_Min | 239 | 40240 | 1 | INT | 0-59
| Shutdown on Friday: hour |  | TimezOffeMng.Off_Fri_Hour | 240 | 40241 | 1 | INT | 0-23
| Shutdown on Friday: minutes |  | TimezOffeMng.Off_Fri_Min | 241 | 40242 | 1 | INT | 0-59
| Shutdown on Saturday: hour |  | TimezOffeMng.Off_Sat_Hour | 242 | 40243 | 1 | INT | 0-23
| Shutdown on Saturday: minutes |  | TimezOffeMng.Off_Sat_Min | 243 | 40244 | 1 | INT | 0-59
| Shutdown on Sunday: hour |  | TimezOffeMng.Off_Sun_Hour | 244 | 40245 | 1 | INT | 0-23
| Shutdown on Sunday: minutes |  | TimezOffeMng.Off_Sun_Min | 245 | 40246 | 1 | INT | 0-59
Time Zone 1 Management | Hour |  | TimezoneMng.TempHr1 | 246 | 40247 | 1 | INT | 0-23
| branch |  | TimezoneMng.TempMin1 | 247 | 40248 | 1 | INT | 0-59
| refrigeration |  | TimezoneMng.S_Set_Temp1 | 248 | 40249 | 1 | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp1 | 249 | 40250 | 1 | REAL | -99.0~99.0
Time Zone 2 Management | Hour |  | TimezoneMng.TempHr2 | 250 | 40251 | 1 | INT | 0-95
| branch |  | TimezoneMng.TempMin2 | 251 | 40252 | 1 | INT | 0-131
| refrigeration |  | TimezoneMng.S_Set_Temp2 | 252 | 40253 | 1 | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp2 | 253 | 40254 | 1 | REAL | -99.0~99.0
Time Zone 3 Management | Hour |  | TimezoneMng.TempHr3 | 254 | 40255 | 1 | INT | 0-167
| branch |  | TimezoneMng.TempMin3 | 255 | 40256 | 1 | INT | 0-203
| refrigeration |  | TimezoneMng.S_Set_Temp3 | 256 | 40257 | 1 | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp3 | 257 | 40258 | 1 | REAL | -99.0~99.0
Time Zone 4 Management | Hour |  | TimezoneMng.TempHr4 | 258 | 40259 | 1 | INT | 0-239
| branch |  | TimezoneMng.TempMin4 | 259 | 40260 | 1 | INT | 0-275
| refrigeration |  | TimezoneMng.S_Set_Temp4 | 260 | 40261 | 1 | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp4 | 261 | 40262 | 1 | REAL | -99.0~99.0
|  | EEV2 manual steps | EVI_ManSteps | 262 | 40263 | 1 | int | 0-480
Fan Economy Mode | Cooling ambient temperature X-axis setting | X1 | X_CH[1] | 276 | 40277 | 1 | real | -99.9~99.9
|  | X2 | X_CH[2] | 277 | 40278 | 1 | real | -99.9~99.9
|  | X3 | X_CH[3] | 278 | 40279 | 1 | real | -99.9~99.9
|  | X4 | X_CH[4] | 279 | 40280 | 1 | real | -99.9~99.9
| Heating ambient temperature X-axis setting | X1 | X_Hp[1] | 280 | 40281 | 1 | real | -99.9~99.9
|  | X2 | X_Hp[2] | 281 | 40282 | 1 | real | -99.9~99.9
|  | X3 | X_Hp[3] | 282 | 40283 | 1 | real | -99.9~99.9
|  | X4 | X_Hp[4] | 283 | 40284 | 1 | real | -99.9~99.9
| Hot water ambient temperature X-axis setting | X1 | X_DHW[1] | 284 | 40285 | 1 | real | -99.9~99.9
|  | X2 | X_DHW[2] | 285 | 40286 | 1 | real | -99.9~99.9
|  | X3 | X_DHW[3] | 286 | 40287 | 1 | real | -99.9~99.9
|  | X4 | X_DHW[4] | 287 | 40288 | 1 | real | -99.9~99.9
| Cooling water temperature Y-axis setting point | Y2 | Y_CH[2] | 288 | 40289 | 1 | real | -99.9~99.9
|  | Y3 | Y_CH[3] | 289 | 40290 | 1 | real | -99.9~99.9
|  | Y4 | Y_CH[4] | 290 | 40291 | 1 | real | -99.9~99.9
| Heating water temperature Y-axis setting point | Y1 | Y_Hp[1] | 291 | 40292 | 1 | real | -99.9~99.9
|  | Y2 | Y_Hp[2] | 292 | 40293 | 1 | real | -99.9~99.9
|  | Y3 | Y_Hp[3] | 293 | 40294 | 1 | real | -99.9~99.9
| Hot water temperature Y-axis setting point | Y1 | Y_DHW[1] | 294 | 40295 | 1 | real | -99.9~99.9
|  | Y2 | Y_DHW[2] | 295 | 40296 | 1 | real | -99.9~99.9
|  | Y3 | Y_DHW[3] | 296 | 40297 | 1 | real | -99.9~99.9
|  | Setting point for environmental temperature switching mode | Amb_switch_SetP | 297 | 40298 | 1 | real | 10.0~30.0
|  | Loop temperature switching mode return difference | Amb_switch_Offs | 298 | 40299 | 1 | real | 0.0~20.0
|  | Minimum start interval of water pump | MIN_pumpoffTime | 299 | 40300 | 1 | int | 1~99min
|  | Correction value of return water temperature | CW_InTemp_Offs | 300 | 40301 | 1 | real | 0.0~99.0
|  | Correction value of outlet water temperature | CW_OutTemp_Offs | 301 | 40302 | 1 | real | 0.0~99.0
|  | Ambient temp correction value | AmbTemp_Offs | 302 | 40303 | 1 | real | 0.0~99.0
|  | Exhaust temperature correction value | DscgTemp_Offs | 303 | 40304 | 1 | real | 0.0~99.0
|  | Correction value of suction temperature | SuctTemp_Offs | 304 | 40305 | 1 | real | 0.0~99.0
|  | High pressure correction value | DscgP_Offs | 305 | 40306 | 1 | real | 0.0~99.0
|  | Low pressure correction value | SuctP_Offs | 306 | 40307 | 1 | real | 0.0~99.0
|  | Correction value of hot water temperature | Water_Tank_Temp_Offs | 307 | 40308 | 1 | real | 0.0~99.0
|  | Correction value for coil temperature | CondsrCoilTemp_Offs | 308 | 40309 | 1 | real | 0.0~99.0
|  | Electronic expansion valve 2 opening | EVD_Emb_1_2.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | 309 | 40310 | 1 | int | 0-480
|  | High temperature differential load reduction deviation | DeltaTemp_Deload_SetP1 | 310 | 40311 | 1 | real | 0.0-99.0
|  | High temperature difference frequency limiting deviation | DeltaTemp_Deload_SetP2 | 311 | 40312 | 1 | real | 0.0-99.0
|  | High temperature difference frequency limiting exit deviation | DeltaTemp_Deload_SetP3 | 312 | 40313 | 1 | real | 0.0-99.0
|  | Deviation of high water outlet load reduction | OutletHighTemp_Deload_SetP1 | 313 | 40314 | 1 | real | 0.0-99.0
|  | High water outlet frequency limit deviation | OutletHighTemp_Deload_SetP2 | 314 | 40315 | 1 | real | 0.0-99.0
|  | Exit deviation of high water outlet frequency limit | OutletHighTemp_Deload_SetP3 | 315 | 40316 | 1 | real | 0.0-99.0
|  | Deviation of low effluent load reduction | OutletLowTemp_Deload_SetP1 | 316 | 40317 | 1 | real | 0.0-99.0
|  | Low water outlet frequency limit deviation | OutletLowTemp_Deload_SetP2 | 317 | 40318 | 1 | real | 0.0-99.0
|  | Low water outlet frequency limit exit deviation | OutletLowTemp_Deload_SetP3 | 318 | 40319 | 1 | real | 0.0-99.0
|  | Frequency reduction delay | Deloading_delay | 319 | 40320 | 1 | int | 0-99
|  | Frequency reduction status | Deload_Code | 320 | 40321 | 1 | int | 0: 1: High temperature differential frequency limit 2: Low water outlet frequency limit 3: High water outlet frequency limit
|  | Frequency reduction interval | Deload_Interval_time | 321 | 40322 | 1 | int | Unit: seconds
|  | Frequency reduction rate | Deload_rate | 322 | 40323 | 1 | real
|  | Electric heating control | En_AuxHeat | 323 | 40324 | 1 | INT | 0: Disabled 1: Hot water 2: Floor heating 3: Shared
|  | Antifreeze requirements | Anti_CompReq | 324 | 40325 | 1 | real
|  | Program version number 1 | GeneralMng.CurrVer.X | 325 | 40326 | 1 | INT
|  | Program version number 2 | GeneralMng.CurrVer.Y | 326 | 40327 | 1 | INT
|  | Program version number 3 | GeneralMng.CurrVer.Z | 327 | 40328 | 1 | INT
|  | Unit Model Code 1 | GeneralMng.UnitType_A | 328 | 40329 | 1 | INT
|  | Unit Model Code 2 | GeneralMng.UnitType_B | 329 | 40330 | 1 | INT
|  | Delayed start of the water pump for three minutes during fault standby | Alarm_pumpoff_Time | 330 | 40331 | 1 | int | min
|  | During normal standby, delay starting the water pump for three minutes | Unit_StandBy_Anti_Delay | 331 | 40332 | 1 | INT | min
|  | Input and output frequency converter default value | BLDC_Mng.MiscMng_PWRP1.Mng_WriteDefault | 332 | 40333 | 1 | int | 0: No 1: Yes
|  | Frequency converter power | BLDC_Mng.Info_PWRP1.Info_MotPwr | 333 | 40334 | 1 | real
|  | Frequency converter voltage | BLDC_Mng.Info_PWRP1.Info_MotV | 334 | 40335 | 1 | int
|  | Frequency converter current | BLDC_Mng.Info_PWRP1.Info_MotA | 335 | 40336 | 1 | real
| Heating setting point |  | CFchange.HeatSetP_F | 491 | 40492 | 1 | REAL | 50.0~CFchange.heat_set_max_F默认131）范围 | Setpoint ℉ added
| Refrigeration setting point |  | CFchange.CoolSetP_F | 492 | 40493 | 1 | REAL | CFchange.cool_set_min_F（默认53.6）~104范围 | Setpoint ℉ added
| Hot water setting point |  | CFchange.W_TankSetP_F | 493 | 40494 | 1 | REAL | 50.0~CFchange.heat_set_max_F（默认131）范围 | Setpoint ℉ added
1
1
| language | [7 empty] | No such variable
1
1
1

## Sheet3
Holding Registers

## modbus config
interval
Electric heating control | Electric heating control | En_AuxHeat | En_AuxHeat | 0 | 1 | bool | coil | 300 | - { address: 0, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Electric heating control", unique_id: "apollo.En_AuxHeat"} |  | 0: Day mode; 1: Night mode; 2: Low wind mode; 3: Pressure mode; | coil
Crankshaft/chassis electric heating control | Crankshaft/chassis electric heating control | En_Chassis_Crank_Heat | En_Chassis_Crank_Heat | 1 | 2 | bool | coil | 300 | - { address: 1, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Crankshaft/chassis electric heating control", unique_id: "apollo.En_Chassis_Crank_Heat"}
Power-off self start | Power-off self start | OnOffUnitMng.UnitTypAfterPwrOff | OnOffUnitMng_UnitTypAfterPwrOff | 2 | 3 | bool | coil | 300 | - { address: 2, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Power-off self start", unique_id: "apollo.OnOffUnitMng_UnitTypAfterPwrOff"}
Water pump manual | Water pump manual | En_PmpMan | En_PmpMan | 3 | 4 | BOOL | coil | 300 | - { address: 3, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Water pump manual", unique_id: "apollo.En_PmpMan"}
Manual speed control fan | Manual speed control fan | fan_man_en | fan_man_en | 4 | 5 | BOOL | coil | 300 | - { address: 4, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual speed control fan", unique_id: "apollo.fan_man_en"}
Compressor manual | Compressor manual | CompMan | CompMan | 5 | 6 | BOOL | coil | 300 | - { address: 5, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Compressor manual", unique_id: "apollo.CompMan"}
EEV manual | EEV manual | EVD_Manual | EVD_Manual | 6 | 7 | BOOL | coil | 300 | - { address: 6, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - EEV manual", unique_id: "apollo.EVD_Manual"}
Manual four-way valve | Manual four-way valve | ManDout3 | ManDout3 | 7 | 8 | BOOL | coil | 300 | - { address: 7, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual four-way valve", unique_id: "apollo.ManDout3"}
Manual waterway three-way valve | Manual waterway three-way valve | ManDout5 | ManDout5 | 8 | 9 | BOOL | coil | 300 | - { address: 8, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual waterway three-way valve", unique_id: "apollo.ManDout5"}
Manual crankshaft electric heating | Manual crankshaft electric heating | ManDout6 | ManDout6 | 9 | 10 | BOOL | coil | 300 | - { address: 9, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual crankshaft electric heating", unique_id: "apollo.ManDout6"}
Manual chassis electric heating | Manual chassis electric heating | ManDout7 | ManDout7 | 10 | 11 | BOOL | coil | 300 | - { address: 10, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual chassis electric heating", unique_id: "apollo.ManDout7"}
Manual end pump | Manual end pump | ManDout8 | ManDout8 | 11 | 12 | BOOL | coil | 300 | - { address: 11, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual end pump", unique_id: "apollo.ManDout8"}
Manual electric heating | Manual electric heating | ManDout9 | ManDout9 | 12 | 13 | BOOL | coil | 300 | - { address: 12, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual electric heating", unique_id: "apollo.ManDout9"}
Insert frequency converter parameters | Insert frequency converter parameters | Insert_POWER | Insert_POWER | 13 | 14 | BOOL | coil | 300 | - { address: 13, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Insert frequency converter parameters", unique_id: "apollo.Insert_POWER"}
Enable upper machine monitoring | Enable upper machine monitoring | BmsOnOff_En | BmsOnOff_En | 15 | 16 | BOOL | coil | 300 | - { address: 15, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enable upper machine monitoring", unique_id: "apollo.BmsOnOff_En"}
normally open/normally closed | normally open/normally closed | InputsCheck.FlwSw_Logic | InputsCheck_FlwSw_Logic | 16 | 17 | BOOL | coil | 300 | - { address: 16, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - normally open/normally closed", unique_id: "apollo.InputsCheck_FlwSw_Logic"}
| ID2: Emergency switch | InputsCheck.RemoteOnOff_Logic | InputsCheck_RemoteOnOff_Logic | 17 | 18 | BOOL | coil | 300 | - { address: 17, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - ID2: Emergency switch", unique_id: "apollo.InputsCheck_RemoteOnOff_Logic"}
| ID3: End signal switch | InputsCheck.Terminal_Switch_Logic | InputsCheck_Terminal_Switch_Logic | 18 | 19 | BOOL | coil | 300 | - { address: 18, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - ID3: End signal switch", unique_id: "apollo.InputsCheck_Terminal_Switch_Logic"}
| ID5: power phase | InputsCheck.ProtSeqPh_Logic | InputsCheck_ProtSeqPh_Logic | 19 | 20 | BOOL | coil | 300 | - { address: 19, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - ID5: power phase", unique_id: "apollo.InputsCheck_ProtSeqPh_Logic"}
| DO1: High wind | Outputs.FanHiSpeed_Logic | Outputs_FanHiSpeed_Logic | 20 | 21 | BOOL | coil | 300 | - { address: 20, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO1: High wind", unique_id: "apollo.Outputs_FanHiSpeed_Logic"}
| DO2: Low wind | Outputs.FanLowSpeed_Logic | Outputs_FanLowSpeed_Logic | 21 | 22 | BOOL | coil | 300 | - { address: 21, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO2: Low wind", unique_id: "apollo.Outputs_FanLowSpeed_Logic"}
| DO3: Four way valve | FwVlv_On_Logic | FwVlv_On_Logic | 22 | 23 | BOOL | coil | 300 | - { address: 22, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO3: Four way valve", unique_id: "apollo.FwVlv_On_Logic"}
| DO4: Host water pump | Outputs.Pmp_On_Logic | Outputs_Pmp_On_Logic | 23 | 24 | BOOL | coil | 300 | - { address: 23, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO4: Host water pump", unique_id: "apollo.Outputs_Pmp_On_Logic"}
| DO5: Waterway three-way valve | Outputs.ThreeWVlv_Logic | Outputs_ThreeWVlv_Logic | 24 | 25 | BOOL | coil | 300 | - { address: 24, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO5: Waterway three-way valve", unique_id: "apollo.Outputs_ThreeWVlv_Logic"}
| DO6: Electric heating of crankshaft | Outputs.HeatCrack_Logic | Outputs_HeatCrack_Logic | 25 | 26 | BOOL | coil | 300 | - { address: 25, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO6: Electric heating of crankshaft", unique_id: "apollo.Outputs_HeatCrack_Logic"}
| DO7: Chassis electric heating | Outputs.Heat_Chassis_Logic | Outputs_Heat_Chassis_Logic | 26 | 27 | BOOL | coil | 300 | - { address: 26, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO7: Chassis electric heating", unique_id: "apollo.Outputs_Heat_Chassis_Logic"}
| DO8: End pump | Outputs.Terminal_Pump_Logic | Outputs_Terminal_Pump_Logic | 27 | 28 | BOOL | coil | 300 | - { address: 27, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO8: End pump", unique_id: "apollo.Outputs_Terminal_Pump_Logic"}
| DO9: Electric heating | Outputs.AuxHeat_Logic | Outputs_AuxHeat_Logic | 28 | 29 | BOOL | coil | 300 | - { address: 28, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DO9: Electric heating", unique_id: "apollo.Outputs_AuxHeat_Logic"}
Enthalpy increasing valve control mode | Enthalpy increasing valve control mode | EEV2_control_mode | EEV2_control_mode | 29 | 30 | BOOL | coil | 300 | - { address: 29, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enthalpy increasing valve control mode", unique_id: "apollo.EEV2_control_mode"} |  | 0: Inhalation superheat; 1: Exhaust superheat;
Auxiliary electronic expansion valve | Auxiliary electronic expansion valve | EnVaporInj | EnVaporInj | 30 | 31 | BOOL | coil | 300 | - { address: 30, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Auxiliary electronic expansion valve", unique_id: "apollo.EnVaporInj"}
Enable return oil control | Enable return oil control | En_OilRecov | En_OilRecov | 31 | 32 | BOOL | coil | 300 | - { address: 31, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enable return oil control", unique_id: "apollo.En_OilRecov"}
Speed control fan activation | Speed control fan activation | CondenserFan.en_fan_rpm | CondenserFan_en_fan_rpm | 32 | 33 | bool | coil | 300 | - { address: 32, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Speed control fan activation", unique_id: "apollo.CondenserFan_en_fan_rpm"}
Fan communication failure shutdown | Fan communication failure shutdown | en_al_fan_offcom | en_al_fan_offcom | 33 | 34 | bool | coil | 300 | - { address: 33, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Fan communication failure shutdown", unique_id: "apollo.en_al_fan_offcom"}
Enable networking | Enable networking | En_NetWork | En_NetWork | 34 | 35 | bool | coil | 300 | - { address: 34, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enable networking", unique_id: "apollo.En_NetWork"}
Set Unit Category | Set Unit Category | DevicesRotation_mng.MB_Choise | DevicesRotation_mng_MB_Choise | 35 | 36 | bool | coil | 300 | - { address: 35, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Set Unit Category", unique_id: "apollo.DevicesRotation_mng_MB_Choise"} |  | 0: Slave; 1: Host;
Enable defrosting | Enable defrosting | En_DefrostMng | En_DefrostMng | 36 | 37 | BOOL | coil | 300 | - { address: 36, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enable defrosting", unique_id: "apollo.En_DefrostMng"}
Defrost switching four-way valve press compensation | Defrost switching four-way valve press compensation | En_Dfr_PressOffset | En_Dfr_PressOffset | 37 | 38 | BOOL | coil | 300 | - { address: 37, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Defrost switching four-way valve press compensation", unique_id: "apollo.En_Dfr_PressOffset"}
Enable time zone switch on/off | Enable time zone switch on/off | En_SchedOnOff | En_SchedOnOff | 38 | 39 | bool | coil | 300 | - { address: 38, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enable time zone switch on/off", unique_id: "apollo.En_SchedOnOff"}
Enable timed change of setting points | Enable timed change of setting points | En_Sch_Setp | En_Sch_Setp | 39 | 40 | bool | coil | 300 | - { address: 39, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enable timed change of setting points", unique_id: "apollo.En_Sch_Setp"}
Unit switch on/off | Unit switch on/off | OnOffUnitMng.KeybOnOff | OnOffUnitMng_KeybOnOff | 40 | 41 | bool | coil | 300 | - { address: 40, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Unit switch on/off", unique_id: "apollo.OnOffUnitMng_KeybOnOff"} |  | 0: Off 1: On
Alarm reset | Alarm reset | AlrmResByBms | AlrmResByBms | 41 | 42 | BOOL | coil | 300 | - { address: 41, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Alarm reset", unique_id: "apollo.AlrmResByBms"}
Unit mode | Unit mode | en_three_valve | en_three_valve | 42 | 43 | BOOL | coil | 300 | - { address: 42, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Unit mode", unique_id: "apollo.en_three_valve"} |  | 0: Dual supply 1: Triple supply
Enable synchronization | Enable synchronization | En_Date | En_Date | 43 | 44 | bool | coil | 300 | - { address: 43, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enable synchronization", unique_id: "apollo.En_Date"}
on/off | DI4: Refrigeration linkage | InputsCheck.CoolSw_Logic | InputsCheck_CoolSw_Logic | 45 | 46 | BOOL | coil | 300 | - { address: 45, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DI4: Refrigeration linkage", unique_id: "apollo.InputsCheck_CoolSw_Logic"}
| DI5: Heating linkage | InputsCheck.HeatSW_Logic | InputsCheck_HeatSW_Logic | 46 | 47 | BOOL | coil | 300 | - { address: 46, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - DI5: Heating linkage", unique_id: "apollo.InputsCheck_HeatSW_Logic"}
| Speed regulating water pump | PumpMng.Enable_Ao_Pump | PumpMng_Enable_Ao_Pump | 47 | 48 | BOOL | coil | 300 | - { address: 47, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Speed regulating water pump", unique_id: "apollo.PumpMng_Enable_Ao_Pump"} | 0: Disable 1: Enable
| EEV2 manual mode | En_EVI_ManMode | En_EVI_ManMode | 48 | 49 | BOOL | coil | 300 | - { address: 48, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - EEV2 manual mode", unique_id: "apollo.En_EVI_ManMode"} | 0: Disable 1: Enable
| Manual low wind | ManDout1 | ManDout1 | 49 | 50 | BOOL | coil | 300 | - { address: 49, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual low wind", unique_id: "apollo.ManDout1"}
| Manual high wind | ManDout2 | ManDout2 | 50 | 51 | BOOL | coil | 300 | - { address: 50, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Manual high wind", unique_id: "apollo.ManDout2"}
| Fan grading windshield mode | fan_mode_bool | fan_mode_bool | 51 | 52 | BOOL | coil | 300 | - { address: 51, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Fan grading windshield mode", unique_id: "apollo.fan_mode_bool"} | 0: Grading position 1: Grading
| Enable mode switching based on ambient temperature | Enable_AmbTemp_Switch | Enable_AmbTemp_Switch | 52 | 53 | bool | coil | 300 | - { address: 52, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Enable mode switching based on ambient temperature", unique_id: "apollo.Enable_AmbTemp_Switch"} | 0: Disable 1: Enable
| First level antifreeze enable | Enable_Antifreeze_Prevent_first | Enable_Antifreeze_Prevent_first | 53 | 54 | bool | coil | 300 | - { address: 53, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - First level antifreeze enable", unique_id: "apollo.Enable_Antifreeze_Prevent_first"} | 0: Disable 1: Enable
| Secondary antifreeze enable | Enable_Antifreeze_Prevent_sec | Enable_Antifreeze_Prevent_sec | 54 | 55 | bool | coil | 300 | - { address: 54, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Secondary antifreeze enable", unique_id: "apollo.Enable_Antifreeze_Prevent_sec"} | 0: Disable 1: Enable
| Switch from station to hot water mode and enable hot water demand | Enable_HotWater_mode_switch | Enable_HotWater_mode_switch | 55 | 56 | bool | coil | 300 | - { address: 55, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Switch from station to hot water mode and enable hot water demand", unique_id: "apollo.Enable_HotWater_mode_switch"} | 0: Disable 1: Enable
| Restore default values | En_WipeMem | En_WipeMem | 57 | 58 | bool | coil | 300 | - { address: 57, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Restore default values", unique_id: "apollo.En_WipeMem"} | 0: No 1: Yes
| Refrigeration point compensation | Cool_SetPCompensated_enable | Cool_SetPCompensated_enable | 110 | 111 | bool | coil | 300 | - { address: 110, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Refrigeration point compensation", unique_id: "apollo.Cool_SetPCompensated_enable"} | 0: Disable 1: Enable
| Heating point compensation | Heat_SetPCompensated_enable | Heat_SetPCompensated_enable | 111 | 112 | bool | coil | 300 | - { address: 111, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Heating point compensation", unique_id: "apollo.Heat_SetPCompensated_enable"} | 0: Disable 1: Enable
| Hot water point compensation | W_TankSetPCompensated_enable | W_TankSetPCompensated_enable | 112 | 113 | bool | coil | 300 | - { address: 112, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Hot water point compensation", unique_id: "apollo.W_TankSetPCompensated_enable"} | 0: Disable 1: Enable
| Swimming pool switch status | POOL_HeatSw_Din | POOL_HeatSw_Din | 113 | 114 | bool | coil | 300 | - { address: 113, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Swimming pool switch status", unique_id: "apollo.POOL_HeatSw_Din"} | 0: Closed 1: Open
| Heating mode enables swimming pool function | En_pool_heat_heat | En_pool_heat_heat | 114 | 115 | bool | coil | 300 | - { address: 114, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Heating mode enables swimming pool function", unique_id: "apollo.En_pool_heat_heat"} | 0: Disable 1: Enable
| Hot water mode enables swimming pool function | En_pool_heat_hot | En_pool_heat_hot | 115 | 116 | bool | coil | 300 | - { address: 115, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Hot water mode enables swimming pool function", unique_id: "apollo.En_pool_heat_hot"} | 0: Disable 1: Enable
| Heating+hot water mode enables swimming pool function | En_pool_heat_heathot | En_pool_heat_heathot | 116 | 117 | bool | coil | 300 | - { address: 116, scan_interval: 300, input_type: coil, slave: 1, name: "ApolloHP - Heating+hot water mode enables swimming pool function", unique_id: "apollo.En_pool_heat_heathot"} | 0: Disable 1: Enable
Unit mode | Unit mode | UnitOn | UnitOn | 0 | 10001 | BOOL | discrete_input | 300 | - { address: 0, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Unit mode", unique_id: "apollo.UnitOn"}
Water flow switch | Water flow switch | InputsCheck.FlwSw_Din | InputsCheck_FlwSw_Din | 1 | 10002 | BOOL | discrete_input | 300 | - { address: 1, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Water flow switch", unique_id: "apollo.InputsCheck_FlwSw_Din"}
Emergency switch | Emergency switch | InputsCheck.RemoteOnOff_Din | InputsCheck_RemoteOnOff_Din | 2 | 10003 | BOOL | discrete_input | 300 | - { address: 2, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Emergency switch", unique_id: "apollo.InputsCheck_RemoteOnOff_Din"}
End signal switch | End signal switch | InputsCheck.Terminal_Switch_Din | InputsCheck_Terminal_Switch_Din | 3 | 10004 | BOOL | discrete_input | 300 | - { address: 3, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - End signal switch", unique_id: "apollo.InputsCheck_Terminal_Switch_Din"}
Phase sequence protection | Phase sequence protection | InputsCheck.ProtSeqPh_Din | InputsCheck_ProtSeqPh_Din | 4 | 10005 | BOOL | discrete_input | 300 | - { address: 4, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Phase sequence protection", unique_id: "apollo.InputsCheck_ProtSeqPh_Din"}
noble character | noble character | Outputs.DoutVal_1 | Outputs_DoutVal_1 | 5 | 10006 | BOOL | discrete_input | 300 | - { address: 5, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - noble character", unique_id: "apollo.Outputs_DoutVal_1"}
Low wind | Low wind | Outputs.DoutVal_2 | Outputs_DoutVal_2 | 6 | 10007 | BOOL | discrete_input | 300 | - { address: 6, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Low wind", unique_id: "apollo.Outputs_DoutVal_2"}
Four way valve | Four way valve | Outputs.DoutVal_3 | Outputs_DoutVal_3 | 7 | 10008 | BOOL | discrete_input | 300 | - { address: 7, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Four way valve", unique_id: "apollo.Outputs_DoutVal_3"}
Main engine water pump | Main engine water pump | Outputs.DoutVal_4 | Outputs_DoutVal_4 | 8 | 10009 | BOOL | discrete_input | 300 | - { address: 8, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Main engine water pump", unique_id: "apollo.Outputs_DoutVal_4"}
Three way valve | Three way valve | Outputs.DoutVal_5 | Outputs_DoutVal_5 | 9 | 10010 | BOOL | discrete_input | 300 | - { address: 9, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Three way valve", unique_id: "apollo.Outputs_DoutVal_5"}
Electric heating of crankshaft | Electric heating of crankshaft | Outputs.DoutVal_6 | Outputs_DoutVal_6 | 10 | 10011 | BOOL | discrete_input | 300 | - { address: 10, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Electric heating of crankshaft", unique_id: "apollo.Outputs_DoutVal_6"}
Chassis electric heating | Chassis electric heating | Outputs.DoutVal_7 | Outputs_DoutVal_7 | 11 | 10012 | BOOL | discrete_input | 300 | - { address: 11, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Chassis electric heating", unique_id: "apollo.Outputs_DoutVal_7"}
Electric heating | Electric heating | Outputs.DoutVal_9 | Outputs_DoutVal_9 | 12 | 10013 | BOOL | discrete_input | 300 | - { address: 12, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Electric heating", unique_id: "apollo.Outputs_DoutVal_9"}
AL001 | AL001 | Too many mem writings | Too_many_mem_writings | 13 | 10014 | BOOL | discrete_input | 300 | - { address: 13, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL001", unique_id: "apollo.Too_many_mem_writings"} |  | Frequent writing of storage type variables
AL002 | AL002 | Retain mem write error | Retain_mem_write_error | 14 | 10015 | BOOL | discrete_input | 300 | - { address: 14, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL002", unique_id: "apollo.Retain_mem_write_error"} |  | Frequent write error alarms for stored variables
AL003 | AL003 | Inlet probe error | Inlet_probe_error | 15 | 10016 | BOOL | discrete_input | 300 | - { address: 15, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL003", unique_id: "apollo.Inlet_probe_error"} |  | Inlet temperature probe faulty or offline
AL004 | AL004 | Outlet probe error | Outlet_probe_error | 16 | 10017 | BOOL | discrete_input | 300 | - { address: 16, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL004", unique_id: "apollo.Outlet_probe_error"} |  | Faulty or offline outlet temperature probe
AL005 | AL005 | Ambient probe error | Ambient_probe_error | 17 | 10018 | BOOL | discrete_input | 300 | - { address: 17, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL005", unique_id: "apollo.Ambient_probe_error"} |  | Ambient temp probe malfunction or offline
AL006 | AL006 | Condenser coil temp | Condenser_coil_temp | 18 | 10019 | BOOL | discrete_input | 300 | - { address: 18, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL006", unique_id: "apollo.Condenser_coil_temp"} |  | Condensation coil temperature probe faulty or offline
AL007 | AL007 | Water flow switch | Water_flow_switch | 19 | 10020 | BOOL | discrete_input | 300 | - { address: 19, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL007", unique_id: "apollo.Water_flow_switch"} |  | Water flow switch alarm
AL008 | AL008 | Phase sequ.prot.alarm | Phase_sequ_prot_alarm | 20 | 10021 | BOOL | discrete_input | 300 | - { address: 20, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL008", unique_id: "apollo.Phase_sequ_prot_alarm"} |  | Phase sequence protection switch alarm
AL009 | AL009 | Unit work hour warning | Unit_work_hour_warning | 21 | 10022 | BOOL | discrete_input | 300 | - { address: 21, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL009", unique_id: "apollo.Unit_work_hour_warning"} |  | Unit working time warning
AL010 | AL010 | Pump work hour warning | Pump_work_hour_warning | 22 | 10023 | BOOL | discrete_input | 300 | - { address: 22, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL010", unique_id: "apollo.Pump_work_hour_warning"} |  | Water pump working time warning
AL011 | AL011 | Comp.work hour warning | Comp_work_hour_warning | 23 | 10024 | BOOL | discrete_input | 300 | - { address: 23, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL011", unique_id: "apollo.Comp_work_hour_warning"} |  | Compressor working time warning
AL012 | AL012 | Cond.fan work hourWarn | Cond_fan_work_hourWarn | 24 | 10025 | BOOL | discrete_input | 300 | - { address: 24, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL012", unique_id: "apollo.Cond_fan_work_hourWarn"} |  | Working time of condensing fan
AL013 | AL013 | Low superheat - Vlv.A | Low_superheat_Vlv_A | 25 | 10026 | BOOL | discrete_input | 300 | - { address: 25, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL013", unique_id: "apollo.Low_superheat_Vlv_A"} |  | EEV valve A low superheat alarm
AL014 | AL014 | Low superheat - Vlv.B | Low_superheat_Vlv_B | 26 | 10027 | BOOL | discrete_input | 300 | - { address: 26, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL014", unique_id: "apollo.Low_superheat_Vlv_B"} |  | EEV valve B low superheat alarm
AL015 | AL015 | LOP - Vlv.A | LOP_Vlv_A | 27 | 10028 | BOOL | discrete_input | 300 | - { address: 27, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL015", unique_id: "apollo.LOP_Vlv_A"} |  | EEV valve A LOP alarm
AL016 | AL016 | LOP - Vlv.B | LOP_Vlv_B | 28 | 10029 | BOOL | discrete_input | 300 | - { address: 28, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL016", unique_id: "apollo.LOP_Vlv_B"} |  | EEV valve B LOP alarm
AL017 | AL017 | MOP - Vlv.A | MOP_Vlv_A | 29 | 10030 | BOOL | discrete_input | 300 | - { address: 29, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL017", unique_id: "apollo.MOP_Vlv_A"} |  | EEV valve A MOP alarm
AL018 | AL018 | MOP - Vlv.B | MOP_Vlv_B | 30 | 10031 | BOOL | discrete_input | 300 | - { address: 30, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL018", unique_id: "apollo.MOP_Vlv_B"} |  | EEV valve B MOP alarm
AL019 | AL019 | Motor error - Vlv.A | Motor_error_Vlv_A | 31 | 10032 | BOOL | discrete_input | 300 | - { address: 31, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL019", unique_id: "apollo.Motor_error_Vlv_A"} |  | EEV valve A alarm
AL020 | AL020 | Motor error - Vlv.B | Motor_error_Vlv_B | 32 | 10033 | BOOL | discrete_input | 300 | - { address: 32, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL020", unique_id: "apollo.Motor_error_Vlv_B"} |  | EEV valve B alarm
AL021 | AL021 | Low suct.temp. - Vlv.A | Low_suct_temp_Vlv_A | 33 | 10034 | BOOL | discrete_input | 300 | - { address: 33, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL021", unique_id: "apollo.Low_suct_temp_Vlv_A"} |  | EEV valve A low suction temperature alarm
AL022 | AL022 | Low suct.temp. - Vlv.B | Low_suct_temp_Vlv_B | 34 | 10035 | BOOL | discrete_input | 300 | - { address: 34, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL022", unique_id: "apollo.Low_suct_temp_Vlv_B"} |  | EEV valve B low suction temperature alarm
AL023 | AL023 | High condens.temp.EVD | High_condens_temp_EVD | 35 | 10036 | BOOL | discrete_input | 300 | - { address: 35, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL023", unique_id: "apollo.High_condens_temp_EVD"} |  | EEV high condensation temperature alarm
AL024 | AL024 | Probe S1 error EVD | Probe_S1_error_EVD | 36 | 10037 | BOOL | discrete_input | 300 | - { address: 36, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL024", unique_id: "apollo.Probe_S1_error_EVD"} |  | EEV S1 probe alarm
AL025 | AL025 | Probe S2 error EVD | Probe_S2_error_EVD | 37 | 10038 | BOOL | discrete_input | 300 | - { address: 37, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL025", unique_id: "apollo.Probe_S2_error_EVD"} |  | EEV S2 probe alarm
AL026 | AL026 | Probe S3 error EVD | Probe_S3_error_EVD | 38 | 10039 | BOOL | discrete_input | 300 | - { address: 38, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL026", unique_id: "apollo.Probe_S3_error_EVD"} |  | EEV S3 probe alarm
AL027 | AL027 | Probe S4 error EVD | Probe_S4_error_EVD | 39 | 10040 | BOOL | discrete_input | 300 | - { address: 39, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL027", unique_id: "apollo.Probe_S4_error_EVD"} |  | EEV S4 probe alarm
AL028 | AL028 | Battery discharge EVD | Battery_discharge_EVD | 40 | 10041 | BOOL | discrete_input | 300 | - { address: 40, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL028", unique_id: "apollo.Battery_discharge_EVD"} |  | EEV battery failure
AL029 | AL029 | EEPROM alarm EVD | EEPROM_alarm_EVD | 41 | 10042 | BOOL | discrete_input | 300 | - { address: 41, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL029", unique_id: "apollo.EEPROM_alarm_EVD"} |  | EEV EEPROM alarm
AL030 | AL030 | Incomplete closing EVD | Incomplete_closing_EVD | 42 | 10043 | BOOL | discrete_input | 300 | - { address: 42, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL030", unique_id: "apollo.Incomplete_closing_EVD"} |  | EEV not fully closed alarm
AL031 | AL031 | Emergency closing EVD | Emergency_closing_EVD | 43 | 10044 | BOOL | discrete_input | 300 | - { address: 43, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL031", unique_id: "apollo.Emergency_closing_EVD"} |  | EEV emergency shutdown alarm
AL032 | AL032 | FW not compatible EVD | FW_not_compatible_EVD | 44 | 10045 | BOOL | discrete_input | 300 | - { address: 44, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL032", unique_id: "apollo.FW_not_compatible_EVD"} |  | EEV FW version mismatch
AL033 | AL033 | Config. error EVD | Config_error_EVD | 45 | 10046 | BOOL | discrete_input | 300 | - { address: 45, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL033", unique_id: "apollo.Config_error_EVD"} |  | EEV configuration error
AL034 | AL034 | EVD Driver offline | EVD_Driver_offline | 46 | 10047 | BOOL | discrete_input | 300 | - { address: 46, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL034", unique_id: "apollo.EVD_Driver_offline"} |  | EEV offline alarm
AL035 | AL035 | BLDC-alarm:High startup DeltaP | BLDC_alarm_High_startup_DeltaP | 47 | 10048 | BOOL | discrete_input | 300 | - { address: 47, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL035", unique_id: "apollo.BLDC_alarm_High_startup_DeltaP"} |  | BLDC - Starting pressure difference too high
AL036 | AL036 | BLDC-alarm:Compressor shut off | BLDC_alarm_Compressor_shut_off | 48 | 10049 | BOOL | discrete_input | 300 | - { address: 48, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL036", unique_id: "apollo.BLDC_alarm_Compressor_shut_off"} |  | BLDC Compressor Off
AL037 | AL037 | BLDC-alarm:Out of Envelope | BLDC_alarm_Out_of_Envelope | 49 | 10050 | BOOL | discrete_input | 300 | - { address: 49, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL037", unique_id: "apollo.BLDC_alarm_Out_of_Envelope"} |  | BLDC - out of operating range
AL038 | AL038 | BLDC-alarm:Starting fail wait | BLDC_alarm_Starting_fail_wait | 50 | 10051 | BOOL | discrete_input | 300 | - { address: 50, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL038", unique_id: "apollo.BLDC_alarm_Starting_fail_wait"} |  | BLDC Compressor Start Failure
AL039 | AL039 | BLDC-alarm:Starting fail exceeded | BLDC_alarm_Starting_fail_exceeded | 51 | 10052 | BOOL | discrete_input | 300 | - { address: 51, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL039", unique_id: "apollo.BLDC_alarm_Starting_fail_exceeded"} |  | BLDC Compressor Start Failure
AL040 | AL040 | BLDC-alarm:Low delta pressure | BLDC_alarm_Low_delta_pressure | 52 | 10053 | BOOL | discrete_input | 300 | - { address: 52, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL040", unique_id: "apollo.BLDC_alarm_Low_delta_pressure"} |  | BLDC Low Pressure Differential
AL041 | AL041 | BLDC-alarm:High discarge gas temp | BLDC_alarm_High_discarge_gas_temp | 53 | 10054 | BOOL | discrete_input | 300 | - { address: 53, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL041", unique_id: "apollo.BLDC_alarm_High_discarge_gas_temp"} |  | BLDC High Exhaust Temperature
AL042 | AL042 | Envelope-alarm:High compressor ratio | Envelope_alarm_High_compressor_ratio | 54 | 10055 | BOOL | discrete_input | 300 | - { address: 54, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL042", unique_id: "apollo.Envelope_alarm_High_compressor_ratio"} |  | Envelope High voltage ratio
AL043 | AL043 | Envelope-alarm:High discharge press. | Envelope_alarm_High_discharge_press_ | 55 | 10056 | BOOL | discrete_input | 300 | - { address: 55, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL043", unique_id: "apollo.Envelope_alarm_High_discharge_press_"} |  | Envelope - High exhaust pressure
AL044 | AL044 | Envelope-alarm:High current | Envelope_alarm_High_current | 56 | 10057 | BOOL | discrete_input | 300 | - { address: 56, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL044", unique_id: "apollo.Envelope_alarm_High_current"} |  | Envelope - High current
AL045 | AL045 | Envelope-alarm:High suction pressure | Envelope_alarm_High_suction_pressure | 57 | 10058 | BOOL | discrete_input | 300 | - { address: 57, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL045", unique_id: "apollo.Envelope_alarm_High_suction_pressure"} |  | Envelope - High suction pressure
AL046 | AL046 | Envelope-alarm:Low compressor ratio | Envelope_alarm_Low_compressor_ratio | 58 | 10059 | BOOL | discrete_input | 300 | - { address: 58, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL046", unique_id: "apollo.Envelope_alarm_Low_compressor_ratio"} |  | Envelope - Low voltage ratio
AL047 | AL047 | Envelope-alarm:Low pressure diff | Envelope_alarm_Low_pressure_diff | 59 | 10060 | BOOL | discrete_input | 300 | - { address: 59, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL047", unique_id: "apollo.Envelope_alarm_Low_pressure_diff"} |  | Envelope - Low pressure difference
AL048 | AL048 | Envelope-alarm:Low discharge pressure | Envelope_alarm_Low_discharge_pressure | 60 | 10061 | BOOL | discrete_input | 300 | - { address: 60, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL048", unique_id: "apollo.Envelope_alarm_Low_discharge_pressure"} |  | Envelope - Low exhaust pressure
AL049 | AL049 | Envelope-alarm:Low suction pressure | Envelope_alarm_Low_suction_pressure | 61 | 10062 | BOOL | discrete_input | 300 | - { address: 61, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL049", unique_id: "apollo.Envelope_alarm_Low_suction_pressure"} |  | Envelope - Low suction pressure
AL050 | AL050 | Envelope-alarm:High discharge temp | Envelope_alarm_High_discharge_temp | 62 | 10063 | BOOL | discrete_input | 300 | - { address: 62, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL050", unique_id: "apollo.Envelope_alarm_High_discharge_temp"} |  | Envelope - High exhaust temperature
AL051 | AL051 | Power+ alarm:01-Overcurrent | Power_alarm_01_Overcurrent | 63 | 10064 | BOOL | discrete_input | 300 | - { address: 63, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL051", unique_id: "apollo.Power_alarm_01_Overcurrent"} |  | Power+01- Overcurrent
AL052 | AL052 | Power+ alarm:02-Motor overload | Power_alarm_02_Motor_overload | 64 | 10065 | BOOL | discrete_input | 300 | - { address: 64, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL052", unique_id: "apollo.Power_alarm_02_Motor_overload"} |  | Power+02- Motor overload
AL053 | AL053 | Power+ alarm:03-DCbus overvoltage | Power_alarm_03_DCbus_overvoltage | 65 | 10066 | BOOL | discrete_input | 300 | - { address: 65, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL053", unique_id: "apollo.Power_alarm_03_DCbus_overvoltage"} |  | Power+03-DCbus overvoltage
AL054 | AL054 | Power+ alarm:04-DCbus undervoltage | Power_alarm_04_DCbus_undervoltage | 66 | 10067 | BOOL | discrete_input | 300 | - { address: 66, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL054", unique_id: "apollo.Power_alarm_04_DCbus_undervoltage"} |  | Power+04-DCbus undervoltage
AL055 | AL055 | Power+ alarm:05-Drive overtemp | Power_alarm_05_Drive_overtemp | 67 | 10068 | BOOL | discrete_input | 300 | - { address: 67, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL055", unique_id: "apollo.Power_alarm_05_Drive_overtemp"} |  | Power+05- Frequency converter overheating
AL056 | AL056 | Power+ alarm:06-Drive undertemp | Power_alarm_06_Drive_undertemp | 68 | 10069 | BOOL | discrete_input | 300 | - { address: 68, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL056", unique_id: "apollo.Power_alarm_06_Drive_undertemp"} |  | Power+06- Inverter under temperature
AL057 | AL057 | Power+ alarm:07-Overcurrent HW | Power_alarm_07_Overcurrent_HW | 69 | 10070 | BOOL | discrete_input | 300 | - { address: 69, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL057", unique_id: "apollo.Power_alarm_07_Overcurrent_HW"} |  | Power+07- Overcurrent HW
AL058 | AL058 | Power+ alarm:08-Motor overtemp | Power_alarm_08_Motor_overtemp | 70 | 10071 | BOOL | discrete_input | 300 | - { address: 70, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL058", unique_id: "apollo.Power_alarm_08_Motor_overtemp"} |  | Power+08- Motor overheating
AL059 | AL059 | Power+ alarm:09-IGBT module error | Power_alarm_09_IGBT_module_error | 71 | 10072 | BOOL | discrete_input | 300 | - { address: 71, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL059", unique_id: "apollo.Power_alarm_09_IGBT_module_error"} |  | Power+09-IGBT module failure
AL060 | AL060 | Power+ alarm:10-CPU error | Power_alarm_10_CPU_error | 72 | 10073 | BOOL | discrete_input | 300 | - { address: 72, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL060", unique_id: "apollo.Power_alarm_10_CPU_error"} |  | Power+10 CPU failure
AL061 | AL061 | Power+ alarm:11-Parameter default | Power_alarm_11_Parameter_default | 73 | 10074 | BOOL | discrete_input | 300 | - { address: 73, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL061", unique_id: "apollo.Power_alarm_11_Parameter_default"} |  | Power+11- Missing parameter
AL062 | AL062 | Power+ alarm:12-DCbus ripple | Power_alarm_12_DCbus_ripple | 74 | 10075 | BOOL | discrete_input | 300 | - { address: 74, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL062", unique_id: "apollo.Power_alarm_12_DCbus_ripple"} |  | Power+12- Bus voltage fluctuation
AL063 | AL063 | Power+ alarm:13-Data comm. Fault | Power_alarm_13_Data_comm_Fault | 75 | 10076 | BOOL | discrete_input | 300 | - { address: 75, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL063", unique_id: "apollo.Power_alarm_13_Data_comm_Fault"} |  | Power+13- Data communication failure
AL064 | AL064 | Power+ alarm:14-Thermistor fault | Power_alarm_14_Thermistor_fault | 76 | 10077 | BOOL | discrete_input | 300 | - { address: 76, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL064", unique_id: "apollo.Power_alarm_14_Thermistor_fault"} |  | Power+14- Thermistor fault
AL065 | AL065 | Power+ alarm:15-Autotuning fault | Power_alarm_15_Autotuning_fault | 77 | 10078 | BOOL | discrete_input | 300 | - { address: 77, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL065", unique_id: "apollo.Power_alarm_15_Autotuning_fault"} |  | Power+15- automatic adjustment fault
AL066 | AL066 | Power+ alarm:16-Drive disabled | Power_alarm_16_Drive_disabled | 78 | 10079 | BOOL | discrete_input | 300 | - { address: 78, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL066", unique_id: "apollo.Power_alarm_16_Drive_disabled"} |  | Power+16- frequency converter disabled
AL067 | AL067 | Power+ alarm:17-Motor phase fault | Power_alarm_17_Motor_phase_fault | 79 | 10080 | BOOL | discrete_input | 300 | - { address: 79, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL067", unique_id: "apollo.Power_alarm_17_Motor_phase_fault"} |  | Power+17- Motor phase sequence fault
AL068 | AL068 | Power+ alarm:18-Internal fan fault | Power_alarm_18_Internal_fan_fault | 80 | 10081 | BOOL | discrete_input | 300 | - { address: 80, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL068", unique_id: "apollo.Power_alarm_18_Internal_fan_fault"} |  | Power+18- Fan fault
AL069 | AL069 | Power+ alarm:19-Speed fault | Power_alarm_19_Speed_fault | 81 | 10082 | BOOL | discrete_input | 300 | - { address: 81, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL069", unique_id: "apollo.Power_alarm_19_Speed_fault"} |  | Power+19- Speed fault
AL070 | AL070 | Power+ alarm:20-PFC module error | Power_alarm_20_PFC_module_error | 82 | 10083 | BOOL | discrete_input | 300 | - { address: 82, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL070", unique_id: "apollo.Power_alarm_20_PFC_module_error"} |  | Power+20-PFC module failure
AL071 | AL071 | Power+ alarm:21-PFC overvoltage | Power_alarm_21_PFC_overvoltage | 83 | 10084 | BOOL | discrete_input | 300 | - { address: 83, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL071", unique_id: "apollo.Power_alarm_21_PFC_overvoltage"} |  | Power+21-PFC overvoltage
AL072 | AL072 | Power+ alarm:22-PFC undervoltage | Power_alarm_22_PFC_undervoltage | 84 | 10085 | BOOL | discrete_input | 300 | - { address: 84, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL072", unique_id: "apollo.Power_alarm_22_PFC_undervoltage"} |  | Power+22-PFC undervoltage
AL073 | AL073 | Power+ alarm:23-STO DetectionError | Power_alarm_23_STO_DetectionError | 85 | 10086 | BOOL | discrete_input | 300 | - { address: 85, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL073", unique_id: "apollo.Power_alarm_23_STO_DetectionError"} |  | Power+23-STO error detection
AL074 | AL074 | Power+ alarm:24-STO DetectionError | Power_alarm_24_STO_DetectionError | 86 | 10087 | BOOL | discrete_input | 300 | - { address: 86, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL074", unique_id: "apollo.Power_alarm_24_STO_DetectionError"} |  | Power+24-STO error detection
AL075 | AL075 | Power+ alarm:25-Ground fault | Power_alarm_25_Ground_fault | 87 | 10088 | BOOL | discrete_input | 300 | - { address: 87, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL075", unique_id: "apollo.Power_alarm_25_Ground_fault"} |  | Power+25- Ground wire fault
AL076 | AL076 | Power+ alarm:26-Internal error 1 | Power_alarm_26_Internal_error_1 | 88 | 10089 | BOOL | discrete_input | 300 | - { address: 88, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL076", unique_id: "apollo.Power_alarm_26_Internal_error_1"} |  | Power+26-CPU synchronization error 1
AL077 | AL077 | Power+ alarm:27-Internal error 2 | Power_alarm_27_Internal_error_2 | 89 | 10090 | BOOL | discrete_input | 300 | - { address: 89, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL077", unique_id: "apollo.Power_alarm_27_Internal_error_2"} |  | Power+27-CPU synchronization error 2
AL078 | AL078 | Power+ alarm:28-Drive overload | Power_alarm_28_Drive_overload | 90 | 10091 | BOOL | discrete_input | 300 | - { address: 90, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL078", unique_id: "apollo.Power_alarm_28_Drive_overload"} |  | Power+28- Inverter overload
AL079 | AL079 | Power+ alarm:29-uC safety fault | Power_alarm_29_uC_safety_fault | 91 | 10092 | BOOL | discrete_input | 300 | - { address: 91, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL079", unique_id: "apollo.Power_alarm_29_uC_safety_fault"} |  | Power+29：uC safety fault
AL080 | AL080 | Power+ alarm:98-Unexpected restart | Power_alarm_98_Unexpected_restart | 92 | 10093 | BOOL | discrete_input | 300 | - { address: 92, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL080", unique_id: "apollo.Power_alarm_98_Unexpected_restart"} |  | Power+98：Unexpected restart
AL081 | AL081 | Power+ alarm:99-Unexpected stop | Power_alarm_99_Unexpected_stop | 93 | 10094 | BOOL | discrete_input | 300 | - { address: 93, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL081", unique_id: "apollo.Power_alarm_99_Unexpected_stop"} |  | Power+99：Unexpected stop
AL082 | AL082 | Power+ safety alarm:01-Current meas.fault | Power_safety_alarm_01_Current_meas_fault | 94 | 10095 | BOOL | discrete_input | 300 | - { address: 94, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL082", unique_id: "apollo.Power_safety_alarm_01_Current_meas_fault"} |  | Power+ safety alarm:01-Current meas.fault
AL083 | AL083 | Power+ safety alarm:02-Current unbalanced | Power_safety_alarm_02_Current_unbalanced | 95 | 10096 | BOOL | discrete_input | 300 | - { address: 95, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL083", unique_id: "apollo.Power_safety_alarm_02_Current_unbalanced"} |  | Power+ safety alarm:02-Current unbalanced
AL084 | AL084 | Power+ safety alarm:03-Over current | Power_safety_alarm_03_Over_current | 96 | 10097 | BOOL | discrete_input | 300 | - { address: 96, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL084", unique_id: "apollo.Power_safety_alarm_03_Over_current"} |  | Power+ safety alarm:03-Over current
AL085 | AL085 | Power+ safety alarm:04-STO alarm | Power_safety_alarm_04_STO_alarm | 97 | 10098 | BOOL | discrete_input | 300 | - { address: 97, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL085", unique_id: "apollo.Power_safety_alarm_04_STO_alarm"} |  | Power+ safety alarm:04-STO alarm
AL086 | AL086 | Power+ safety alarm:05-STO hardware alarm | Power_safety_alarm_05_STO_hardware_alarm | 98 | 10099 | BOOL | discrete_input | 300 | - { address: 98, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL086", unique_id: "apollo.Power_safety_alarm_05_STO_hardware_alarm"} |  | Power+ safety alarm:05-STO hardware alarm
AL087 | AL087 | Power+ safety alarm:06-PowerSupply missing | Power_safety_alarm_06_PowerSupply_missing | 99 | 10100 | BOOL | discrete_input | 300 | - { address: 99, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL087", unique_id: "apollo.Power_safety_alarm_06_PowerSupply_missing"} |  | Power+ safety alarm:06-PowerSupply missing
AL088 | AL088 | Power+ safety alarm:07-HW fault cmd.buffer | Power_safety_alarm_07_HW_fault_cmd_buffer | 100 | 10101 | BOOL | discrete_input | 300 | - { address: 100, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL088", unique_id: "apollo.Power_safety_alarm_07_HW_fault_cmd_buffer"} |  | Power+ safety alarm:07-HW fault cmd.buffer
AL089 | AL089 | Power+ safety alarm:08-HW fault heater c | Power_safety_alarm_08_HW_fault_heater_c | 101 | 10102 | BOOL | discrete_input | 300 | - { address: 101, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL089", unique_id: "apollo.Power_safety_alarm_08_HW_fault_heater_c"} |  | Power+ safety alarm:08-HW fault heater c.
AL090 | AL090 | Power+ safety alarm:09-Data comm. Fault | Power_safety_alarm_09_Data_comm_Fault | 102 | 10103 | BOOL | discrete_input | 300 | - { address: 102, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL090", unique_id: "apollo.Power_safety_alarm_09_Data_comm_Fault"} |  | Power+ safety alarm:09-Data comm. Fault
AL091 | AL091 | Power+ safety alarm:10-Compr. stall detect | Power_safety_alarm_10_Compr_stall_detect | 103 | 10104 | BOOL | discrete_input | 300 | - { address: 103, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL091", unique_id: "apollo.Power_safety_alarm_10_Compr_stall_detect"} |  | Power+ safety alarm:10-Compr. stall detect
AL092 | AL092 | Power+ safety alarm:11-DCbus over current | Power_safety_alarm_11_DCbus_over_current | 104 | 10105 | BOOL | discrete_input | 300 | - { address: 104, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL092", unique_id: "apollo.Power_safety_alarm_11_DCbus_over_current"} |  | Power+ safety alarm:11-DCbus over current
AL093 | AL093 | Power+ safety alarm:12-HWF DCbus current | Power_safety_alarm_12_HWF_DCbus_current | 105 | 10106 | BOOL | discrete_input | 300 | - { address: 105, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL093", unique_id: "apollo.Power_safety_alarm_12_HWF_DCbus_current"} |  | Power+ safety alarm:12-HWF DCbus current
AL094 | AL094 | Power+ safety alarm:13-DCbus voltage | Power_safety_alarm_13_DCbus_voltage | 106 | 10107 | BOOL | discrete_input | 300 | - { address: 106, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL094", unique_id: "apollo.Power_safety_alarm_13_DCbus_voltage"} |  | Power+ safety alarm:13-DCbus voltage
AL095 | AL095 | Power+ safety alarm:14-HWF DCbus voltage | Power_safety_alarm_14_HWF_DCbus_voltage | 107 | 10108 | BOOL | discrete_input | 300 | - { address: 107, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL095", unique_id: "apollo.Power_safety_alarm_14_HWF_DCbus_voltage"} |  | Power+ safety alarm:14-HWF DCbus voltage
AL096 | AL096 | Power+ safety alarm:15-Input voltage | Power_safety_alarm_15_Input_voltage | 108 | 10109 | BOOL | discrete_input | 300 | - { address: 108, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL096", unique_id: "apollo.Power_safety_alarm_15_Input_voltage"} |  | Power+ safety alarm:15-Input voltage
AL097 | AL097 | Power+ safety alarm:16-HWF input voltage | Power_safety_alarm_16_HWF_input_voltage | 109 | 10110 | BOOL | discrete_input | 300 | - { address: 109, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL097", unique_id: "apollo.Power_safety_alarm_16_HWF_input_voltage"} |  | Power+ safety alarm:16-HWF input voltage
AL098 | AL098 | Power+ safety alarm:17-DCbus power alarm | Power_safety_alarm_17_DCbus_power_alarm | 110 | 10111 | BOOL | discrete_input | 300 | - { address: 110, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL098", unique_id: "apollo.Power_safety_alarm_17_DCbus_power_alarm"} |  | Power+ safety alarm:17-DCbus power alarm
AL099 | AL099 | Power+ safety alarm:18-HWF power mismatch | Power_safety_alarm_18_HWF_power_mismatch | 111 | 10112 | BOOL | discrete_input | 300 | - { address: 111, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL099", unique_id: "apollo.Power_safety_alarm_18_HWF_power_mismatch"} |  | Power+ safety alarm:18-HWF power mismatch
AL100 | AL100 | Power+ safety alarm:19-NTC over temp | Power_safety_alarm_19_NTC_over_temp | 112 | 10113 | BOOL | discrete_input | 300 | - { address: 112, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL100", unique_id: "apollo.Power_safety_alarm_19_NTC_over_temp"} |  | Power+ safety alarm:19-NTC over temp.
AL101 | AL101 | Power+ safety alarm:20-NTC under temp | Power_safety_alarm_20_NTC_under_temp | 113 | 10114 | BOOL | discrete_input | 300 | - { address: 113, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL101", unique_id: "apollo.Power_safety_alarm_20_NTC_under_temp"} |  | Power+ safety alarm:20-NTC under temp.
AL102 | AL102 | Power+ safety alarm:21-NTC fault | Power_safety_alarm_21_NTC_fault | 114 | 10115 | BOOL | discrete_input | 300 | - { address: 114, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL102", unique_id: "apollo.Power_safety_alarm_21_NTC_fault"} |  | Power+ safety alarm:21-NTC fault
AL103 | AL103 | Power+ safety alarm:22-HWF sync fault | Power_safety_alarm_22_HWF_sync_fault | 115 | 10116 | BOOL | discrete_input | 300 | - { address: 115, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL103", unique_id: "apollo.Power_safety_alarm_22_HWF_sync_fault"} |  | Power+ safety alarm:22-HWF sync fault
AL104 | AL104 | Power+ safety alarm:23-Invalid parameter | Power_safety_alarm_23_Invalid_parameter | 116 | 10117 | BOOL | discrete_input | 300 | - { address: 116, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL104", unique_id: "apollo.Power_safety_alarm_23_Invalid_parameter"} |  | Power+ safety alarm:23-Invalid parameter
AL105 | AL105 | Power+ safety alarm:24-FW fault | Power_safety_alarm_24_FW_fault | 117 | 10118 | BOOL | discrete_input | 300 | - { address: 117, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL105", unique_id: "apollo.Power_safety_alarm_24_FW_fault"} |  | Power+ safety alarm:24-FW fault
AL106 | AL106 | Power+ safety alarm:25-HW fault | Power_safety_alarm_25_HW_fault | 118 | 10119 | BOOL | discrete_input | 300 | - { address: 118, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL106", unique_id: "apollo.Power_safety_alarm_25_HW_fault"} |  | Power+ safety alarm:25-HW fault
AL107 | AL107 | Power+ safety alarm:26-reseved | Power_safety_alarm_26_reseved | 119 | 10120 | BOOL | discrete_input | 300 | - { address: 119, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL107", unique_id: "apollo.Power_safety_alarm_26_reseved"} |  | Power+ safety alarm:26-reseved
AL108 | AL108 | Power+ safety alarm:27-reseved | Power_safety_alarm_27_reseved | 120 | 10121 | BOOL | discrete_input | 300 | - { address: 120, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL108", unique_id: "apollo.Power_safety_alarm_27_reseved"} |  | Power+ safety alarm:27-reseved
AL109 | AL109 | Power+ safety alarm:28-reseved | Power_safety_alarm_28_reseved | 121 | 10122 | BOOL | discrete_input | 300 | - { address: 121, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL109", unique_id: "apollo.Power_safety_alarm_28_reseved"} |  | Power+ safety alarm:28-reseved
AL110 | AL110 | Power+ safety alarm:29-reseved | Power_safety_alarm_29_reseved | 122 | 10123 | BOOL | discrete_input | 300 | - { address: 122, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL110", unique_id: "apollo.Power_safety_alarm_29_reseved"} |  | Power+ safety alarm:29-reseved
AL111 | AL111 | Power+ safety alarm:30-reseved | Power_safety_alarm_30_reseved | 123 | 10124 | BOOL | discrete_input | 300 | - { address: 123, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL111", unique_id: "apollo.Power_safety_alarm_30_reseved"} |  | Power+ safety alarm:30-reseved
AL112 | AL112 | Power+ safety alarm:31-reseved | Power_safety_alarm_31_reseved | 124 | 10125 | BOOL | discrete_input | 300 | - { address: 124, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL112", unique_id: "apollo.Power_safety_alarm_31_reseved"} |  | Power+ safety alarm:31-reseved
AL113 | AL113 | Power+ safety alarm:32-reseved | Power_safety_alarm_32_reseved | 125 | 10126 | BOOL | discrete_input | 300 | - { address: 125, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL113", unique_id: "apollo.Power_safety_alarm_32_reseved"} |  | Power+ safety alarm:32-reseved
AL114 | AL114 | Power+ alarm:Power+ offline | Power_alarm_Power_offline | 126 | 10127 | BOOL | discrete_input | 300 | - { address: 126, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL114", unique_id: "apollo.Power_alarm_Power_offline"} |  | Inverter offline alarm
AL115 | AL115 | EEV alarm:Low superheat | EEV_alarm_Low_superheat | 127 | 10128 | BOOL | discrete_input | 300 | - { address: 127, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL115", unique_id: "apollo.EEV_alarm_Low_superheat"} |  | EEV low superheat alarm
AL116 | AL116 | EEV alarm:LOP | EEV_alarm_LOP | 128 | 10129 | BOOL | discrete_input | 300 | - { address: 128, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL116", unique_id: "apollo.EEV_alarm_LOP"} |  | EEV LOP alarm
AL117 | AL117 | EEV alarm:MOP | EEV_alarm_MOP | 129 | 10130 | BOOL | discrete_input | 300 | - { address: 129, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL117", unique_id: "apollo.EEV_alarm_MOP"} |  | EEV MOP alarm
AL118 | AL118 | EEV alarm:High condens.temp | EEV_alarm_High_condens_temp | 130 | 10131 | BOOL | discrete_input | 300 | - { address: 130, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL118", unique_id: "apollo.EEV_alarm_High_condens_temp"} |  | EEV high condensation temperature alarm
AL119 | AL119 | EEV alarm:Low suction temp | EEV_alarm_Low_suction_temp | 131 | 10132 | BOOL | discrete_input | 300 | - { address: 131, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL119", unique_id: "apollo.EEV_alarm_Low_suction_temp"} |  | EEV low suction temperature alarm
AL120 | AL120 | EEV alarm:Motor error | EEV_alarm_Motor_error | 132 | 10133 | BOOL | discrete_input | 300 | - { address: 132, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL120", unique_id: "apollo.EEV_alarm_Motor_error"} |  | EEV motor fault
AL121 | AL121 | EEV alarm:Self Tuning | EEV_alarm_Self_Tuning | 133 | 10134 | BOOL | discrete_input | 300 | - { address: 133, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL121", unique_id: "apollo.EEV_alarm_Self_Tuning"} |  | EEV from  PID error
AL122 | AL122 | EEV alarm:Emergency closing | EEV_alarm_Emergency_closing | 134 | 10135 | BOOL | discrete_input | 300 | - { address: 134, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL122", unique_id: "apollo.EEV_alarm_Emergency_closing"} |  | EEV emergency shutdown alarm
AL123 | AL123 | EEV alarm:Temperature delta | EEV_alarm_Temperature_delta | 135 | 10136 | BOOL | discrete_input | 300 | - { address: 135, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL123", unique_id: "apollo.EEV_alarm_Temperature_delta"} |  | EEV temperature difference protection
AL124 | AL124 | EEV alarm:Pressure delta | EEV_alarm_Pressure_delta | 136 | 10137 | BOOL | discrete_input | 300 | - { address: 136, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL124", unique_id: "apollo.EEV_alarm_Pressure_delta"} |  | EEV differential pressure protection
AL125 | AL125 | EEV alarm:Param.range error | EEV_alarm_Param_range_error | 137 | 10138 | BOOL | discrete_input | 300 | - { address: 137, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL125", unique_id: "apollo.EEV_alarm_Param_range_error"} |  | EEV range error
AL126 | AL126 | EEV alarm:ServicePosit err | EEV_alarm_ServicePosit_err | 138 | 10139 | BOOL | discrete_input | 300 | - { address: 138, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL126", unique_id: "apollo.EEV_alarm_ServicePosit_err"} |  | EEV position signal error
AL127 | AL127 | EEV alarm:ValveID pin error | EEV_alarm_ValveID_pin_error | 139 | 10140 | BOOL | discrete_input | 300 | - { address: 139, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL127", unique_id: "apollo.EEV_alarm_ValveID_pin_error"} |  | EEV serial number error
AL128 | AL128 | Low press alarm | Low_press_alarm | 140 | 10141 | BOOL | discrete_input | 300 | - { address: 140, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL128", unique_id: "apollo.Low_press_alarm"} |  | Low pressure alarm
AL129 | AL129 | High press alarm | High_press_alarm | 141 | 10142 | BOOL | discrete_input | 300 | - { address: 141, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL129", unique_id: "apollo.High_press_alarm"} |  | High voltage alarm
AL130 | AL130 | Disc.temp.probe error | Disc_temp_probe_error | 142 | 10143 | BOOL | discrete_input | 300 | - { address: 142, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL130", unique_id: "apollo.Disc_temp_probe_error"} |  | Exhaust temperature probe alarm
AL131 | AL131 | Suct.temp.probe error | Suct_temp_probe_error | 143 | 10144 | BOOL | discrete_input | 300 | - { address: 143, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL131", unique_id: "apollo.Suct_temp_probe_error"} |  | Suction temperature probe alarm
AL132 | AL132 | Disc.press.probe error | Disc_press_probe_error | 144 | 10145 | BOOL | discrete_input | 300 | - { address: 144, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL132", unique_id: "apollo.Disc_press_probe_error"} |  | Exhaust pressure probe alarm
AL133 | AL133 | Suct.press.probe error | Suct_press_probe_error | 145 | 10146 | BOOL | discrete_input | 300 | - { address: 145, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL133", unique_id: "apollo.Suct_press_probe_error"} |  | Suction pressure probe alarm
AL134 | AL134 | Tank temp.probe error | Tank_temp_probe_error | 146 | 10147 | BOOL | discrete_input | 300 | - { address: 146, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL134", unique_id: "apollo.Tank_temp_probe_error"} |  | Water tank temperature probe alarm
AL135 | AL135 | EVI SuctT.probe error | EVI_SuctT_probe_error | 147 | 10148 | BOOL | discrete_input | 300 | - { address: 147, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL135", unique_id: "apollo.EVI_SuctT_probe_error"} |  | EVI suction temperature probe alarm
AL136 | AL136 | EVI SuctP.probe error | EVI_SuctP_probe_error | 148 | 10149 | BOOL | discrete_input | 300 | - { address: 148, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL136", unique_id: "apollo.EVI_SuctP_probe_error"} |  | EVI suction pressure probe alarm
AL137 | AL137 | Flow switch alarm | Flow_switch_alarm | 149 | 10150 | BOOL | discrete_input | 300 | - { address: 149, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL137", unique_id: "apollo.Flow_switch_alarm"} |  | Water flow switch alarm
AL138 | AL138 | High temp. alarm | High_temp_alarm | 150 | 10151 | BOOL | discrete_input | 300 | - { address: 150, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL138", unique_id: "apollo.High_temp_alarm"} |  | High water outlet temperature alarm
AL139 | AL139 | Low temp. alarm | Low_temp_alarm | 151 | 10152 | BOOL | discrete_input | 300 | - { address: 151, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL139", unique_id: "apollo.Low_temp_alarm"} |  | Low water outlet temperature alarm
AL140 | AL140 | Temp.delta alarm | Temp_delta_alarm | 152 | 10153 | BOOL | discrete_input | 300 | - { address: 152, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL140", unique_id: "apollo.Temp_delta_alarm"} |  | Inlet and outlet water temperature difference alarm
AL141 | AL141 | EVI alarm:Param.range error | EVI_alarm_Param_range_error | 153 | 10154 | BOOL | discrete_input | 300 | - { address: 153, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL141", unique_id: "apollo.EVI_alarm_Param_range_error"} |  | EVI Range Error
AL142 | AL142 | EVI alarm:Low superheat | EVI_alarm_Low_superheat | 154 | 10155 | BOOL | discrete_input | 300 | - { address: 154, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL142", unique_id: "apollo.EVI_alarm_Low_superheat"} |  | EVI low superheat alarm
AL143 | AL143 | EVI alarm:LOP | EVI_alarm_LOP | 155 | 10156 | BOOL | discrete_input | 300 | - { address: 155, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL143", unique_id: "apollo.EVI_alarm_LOP"} |  | EVI LOP alarm
AL144 | AL144 | EVI alarm:MOP | EVI_alarm_MOP | 156 | 10157 | BOOL | discrete_input | 300 | - { address: 156, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL144", unique_id: "apollo.EVI_alarm_MOP"} |  | EVI MOP alarm
AL145 | AL145 | EVI alarm:High condens.temp | EVI_alarm_High_condens_temp | 157 | 10158 | BOOL | discrete_input | 300 | - { address: 157, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL145", unique_id: "apollo.EVI_alarm_High_condens_temp"} |  | EVI high condensation temperature alarm
AL146 | AL146 | EVI alarm:Low suction temp | EVI_alarm_Low_suction_temp | 158 | 10159 | BOOL | discrete_input | 300 | - { address: 158, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL146", unique_id: "apollo.EVI_alarm_Low_suction_temp"} |  | EVI low suction temperature alarm
AL147 | AL147 | EVI alarm:Motor error | EVI_alarm_Motor_error | 159 | 10160 | BOOL | discrete_input | 300 | - { address: 159, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL147", unique_id: "apollo.EVI_alarm_Motor_error"} |  | EVI motor malfunction
AL148 | AL148 | EVI alarm:Self Tuning | EVI_alarm_Self_Tuning | 160 | 10161 | BOOL | discrete_input | 300 | - { address: 160, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL148", unique_id: "apollo.EVI_alarm_Self_Tuning"} |  | EVI adaptive PID error
AL149 | AL149 | EVI alarm:Emergency closing | EVI_alarm_Emergency_closing | 161 | 10162 | BOOL | discrete_input | 300 | - { address: 161, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL149", unique_id: "apollo.EVI_alarm_Emergency_closing"} |  | EVI emergency shutdown
AL150 | AL150 | EVI alarm:ServicePosit% err | EVI_alarm_ServicePosit%_err | 162 | 10163 | BOOL | discrete_input | 300 | - { address: 162, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL150", unique_id: "apollo.EVI_alarm_ServicePosit%_err"} |  | EVI position signal error
AL151 | AL151 | EVI alarm:ValveID pin error | EVI_alarm_ValveID_pin_error | 163 | 10164 | BOOL | discrete_input | 300 | - { address: 163, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL151", unique_id: "apollo.EVI_alarm_ValveID_pin_error"} |  | EVI serial number error
AL152 | AL152 | Supply power error | Supply_power_error | 164 | 10165 | BOOL | discrete_input | 300 | - { address: 164, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL152", unique_id: "apollo.Supply_power_error"} |  | Power frequency fluctuation alarm
AL153 | AL153 | Fan1 fault | Fan1_fault | 165 | 10166 | BOOL | discrete_input | 300 | - { address: 165, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL153", unique_id: "apollo.Fan1_fault"} |  | Speed control fan 1 malfunction
AL154 | AL154 | Fan2 fault | Fan2_fault | 166 | 10167 | BOOL | discrete_input | 300 | - { address: 166, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL154", unique_id: "apollo.Fan2_fault"} |  | Speed control fan 2 malfunction
AL155 | AL155 | Fans Offline | Fans_Offline | 167 | 10168 | BOOL | discrete_input | 300 | - { address: 167, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL155", unique_id: "apollo.Fans_Offline"} |  | Speed control fan communication offline
AL165 | AL165 | Slave1 Offline | Slave1_Offline | 168 | 10169 | BOOL | discrete_input | 300 | - { address: 168, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL165", unique_id: "apollo.Slave1_Offline"} |  | 1 # Slave offline
AL166 | AL166 | Master Offline | Master_Offline | 169 | 10170 | BOOL | discrete_input | 300 | - { address: 169, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL166", unique_id: "apollo.Master_Offline"} |  | Host offline
AL167 | AL167 | Slave2 Offline | Slave2_Offline | 170 | 10171 | BOOL | discrete_input | 300 | - { address: 170, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL167", unique_id: "apollo.Slave2_Offline"} |  | 2 # slave offline
AL168 | AL168 | Slave3 Offline | Slave3_Offline | 171 | 10172 | BOOL | discrete_input | 300 | - { address: 171, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL168", unique_id: "apollo.Slave3_Offline"} |  | 3 # slave offline
AL169 | AL169 | Slave4 Offline | Slave4_Offline | 172 | 10173 | BOOL | discrete_input | 300 | - { address: 172, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL169", unique_id: "apollo.Slave4_Offline"} |  | 4 # slave offline
AL170 | AL170 | Slave5 Offline | Slave5_Offline | 173 | 10174 | BOOL | discrete_input | 300 | - { address: 173, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL170", unique_id: "apollo.Slave5_Offline"} |  | 5 # slave offline
AL171 | AL171 | Slave6 Offline | Slave6_Offline | 174 | 10175 | BOOL | discrete_input | 300 | - { address: 174, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL171", unique_id: "apollo.Slave6_Offline"} |  | 6 # slave offline
AL172 | AL172 | Slave7 Offline | Slave7_Offline | 175 | 10176 | BOOL | discrete_input | 300 | - { address: 175, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL172", unique_id: "apollo.Slave7_Offline"} |  | 7 # slave offline
AL173 | AL173 | Slave8 Offline | Slave8_Offline | 176 | 10177 | BOOL | discrete_input | 300 | - { address: 176, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL173", unique_id: "apollo.Slave8_Offline"} |  | 8 # slave offline
AL174 | AL174 | Slave9 Offline | Slave9_Offline | 177 | 10178 | BOOL | discrete_input | 300 | - { address: 177, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - AL174", unique_id: "apollo.Slave9_Offline"} |  | 9 # slave offline
Water pump switch status | Water pump switch status | Pmp_On | Pmp_On | 178 | 10179 | BOOL | discrete_input | 300 | - { address: 178, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Water pump switch status", unique_id: "apollo.Pmp_On"}
Compressor switch status | Compressor switch status | Comp_On | Comp_On | 179 | 10180 | BOOL | discrete_input | 300 | - { address: 179, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Compressor switch status", unique_id: "apollo.Comp_On"}
Fan switch status | Fan switch status | FanOn | FanOn | 180 | 10181 | BOOL | discrete_input | 300 | - { address: 180, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Fan switch status", unique_id: "apollo.FanOn"}
Refrigeration linkage | (On/Off) | InputsCheck.CoolSw_Din | InputsCheck_CoolSw_Din | 181 | 10182 | BOOL | discrete_input | 300 | - { address: 181, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - (On/Off)", unique_id: "apollo.InputsCheck_CoolSw_Din"}
Heating linkage | (On/Off) | InputsCheck.HeatSW_Din | InputsCheck_HeatSW_Din | 182 | 10183 | BOOL | discrete_input | 300 | - { address: 182, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - (On/Off)", unique_id: "apollo.InputsCheck_HeatSW_Din"}
End water pump | (On/Off) | Outputs.DoutVal_8 | Outputs_DoutVal_8 | 183 | 10184 | BOOL | discrete_input | 300 | - { address: 183, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - (On/Off)", unique_id: "apollo.Outputs_DoutVal_8"}
| Enable high temperature differential frequency limiting | Enable_DeltaTemp_Limit | Enable_DeltaTemp_Limit | 184 | 10185 | bool | discrete_input | 300 | - { address: 184, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Enable high temperature differential frequency limiting", unique_id: "apollo.Enable_DeltaTemp_Limit"}
| Enable low water outlet frequency limiting | Enable_LowOutletTemp_Limit | Enable_LowOutletTemp_Limit | 185 | 10186 | bool | discrete_input | 300 | - { address: 185, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Enable low water outlet frequency limiting", unique_id: "apollo.Enable_LowOutletTemp_Limit"}
| Enable high water outlet frequency limiting | Enable_highOutletTemp_Limit | Enable_highOutletTemp_Limit | 186 | 10187 | bool | discrete_input | 300 | - { address: 186, scan_interval: 300, input_type: discrete_input, slave: 1, name: "ApolloHP - Enable high water outlet frequency limiting", unique_id: "apollo.Enable_highOutletTemp_Limit"}
Working mode | Working mode | CoolHeat_Mode | CoolHeat_Mode | 0 | 40001 | int | holding | 300 | - { address: 0, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Working mode", unique_id: "apollo.CoolHeat_Mode"} | 0~5 | 0: Cooling mode; 1: Heating mode; 2: Hot water mode; 3: Hot water+refrigeration; 4: Hot water+heating; 5: Swimming pool
Heating setting point | Heating setting point | HeatSetP | HeatSetP | 1 | 40002 | REAL | holding | 300 | - { address: 1, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Heating setting point", unique_id: "apollo.HeatSetP"} | 10.0~CoolHeatMng.heat_set_max默认55 | Set value ℃
Refrigeration setting point | Refrigeration setting point | CoolSetP | CoolSetP | 2 | 40003 | REAL | holding | 300 | - { address: 2, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Refrigeration setting point", unique_id: "apollo.CoolSetP"} | CoolHeatMng.cool_set_min默认12~40.0 | Set value ℃
Hot water point setting | Hot water point setting | W_TankSetP | W_TankSetP | 3 | 40004 | REAL | holding | 300 | - { address: 3, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hot water point setting", unique_id: "apollo.W_TankSetP"} | 10.0~CoolHeatMng.heat_set_max默认55 | Set value ℃
Hot water return difference | Hot water return difference | hotwater_start_diff | hotwater_start_diff | 4 | 40005 | REAL | holding | 300 | - { address: 4, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hot water return difference", unique_id: "apollo.hotwater_start_diff"} | 1.0~15.0
Hot water constant temperature shutdown | Hot water constant temperature shutdown | hotwater_stop_diff | hotwater_stop_diff | 5 | 40006 | REAL | holding | 300 | - { address: 5, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hot water constant temperature shutdown", unique_id: "apollo.hotwater_stop_diff"} | 0.0~5.0
Cooling and heating return difference | Cooling and heating return difference | Temp_Diff | Temp_Diff | 6 | 40007 | REAL | holding | 300 | - { address: 6, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Cooling and heating return difference", unique_id: "apollo.Temp_Diff"} | 1.0~15.0
Refrigeration heating constant temperature shutdown | Refrigeration heating constant temperature shutdown | Stop_TemP_Diff | Stop_TemP_Diff | 7 | 40008 | REAL | holding | 300 | - { address: 7, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Refrigeration heating constant temperature shutdown", unique_id: "apollo.Stop_TemP_Diff"} | 0.0~5.0
deviation | deviation | Kp | Kp | 8 | 40009 | REAL | holding | 300 | - { address: 8, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - deviation", unique_id: "apollo.Kp"} | 1.0~999.0
Integral time | Integral time | Ti | Ti | 9 | 40010 | UINT | holding | 300 | - { address: 9, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Integral time", unique_id: "apollo.Ti"} | 0-9999
Differential time | Differential time | Td | Td | 10 | 40011 | UINT | holding | 300 | - { address: 10, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Differential time", unique_id: "apollo.Td"} | 0-9999
Main engine water pump | Main engine water pump | PmpMode | PmpMode | 11 | 40012 | int | holding | 300 | - { address: 11, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main engine water pump", unique_id: "apollo.PmpMode"} | 0~1 | 0: on; 1: Based on demand;
Fan mode | Fan mode | FanMode_Sel | FanMode_Sel | 12 | 40013 | int | holding | 300 | - { address: 12, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Fan mode", unique_id: "apollo.FanMode_Sel"} | 0~3
Electric heating start delay | Electric heating start delay | DT_AuxComp | DT_AuxComp | 13 | 40014 | UINT | holding | 300 | - { address: 13, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Electric heating start delay", unique_id: "apollo.DT_AuxComp"} | 0-999
Electric heating start temperature | Electric heating start temperature | AuxHeatSetP_Exterior | AuxHeatSetP_Exterior | 14 | 40015 | real | holding | 300 | - { address: 14, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Electric heating start temperature", unique_id: "apollo.AuxHeatSetP_Exterior"} | -30.0~20.0
Main water pump control | Speed control inlet and outlet water temperature difference | PmpDeltaTempSetP | PmpDeltaTempSetP | 15 | 40016 | real | holding | 300 | - { address: 15, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Speed control inlet and outlet water temperature difference", unique_id: "apollo.PmpDeltaTempSetP"} | 2.0~15.0
Low pressure alarm delay | start delay | StartUpDT_SuctLowP | StartUpDT_SuctLowP | 16 | 40017 | int | holding | 300 | - { address: 16, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - start delay ", unique_id: "apollo.StartUpDT_SuctLowP"} | 0~999
| Operation delay | DT_SuctLowPrun | DT_SuctLowPrun | 17 | 40018 | int | holding | 300 | - { address: 17, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Operation delay", unique_id: "apollo.DT_SuctLowPrun"} | 0~999
Speed management | Start-up forced speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_StartUpSpeed | BLDC_Mng_CfgEnvCtrl_BLDC1_Speed_StartUpSpeed | 18 | 40019 | REAL | holding | 300 | - { address: 18, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start-up forced speed ", unique_id: "apollo.BLDC_Mng_CfgEnvCtrl_BLDC1_Speed_StartUpSpeed"} | 20.0~120.0
| Max speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_MaxSpeedRpsCustom | BLDC_Mng_CfgEnvCtrl_BLDC1_Speed_MaxSpeedRpsCustom | 19 | 40020 | REAL | holding | 300 | - { address: 19, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Max speed", unique_id: "apollo.BLDC_Mng_CfgEnvCtrl_BLDC1_Speed_MaxSpeedRpsCustom"} | 0.0~999.0
| Min speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_MinSpeedRpsCustom | BLDC_Mng_CfgEnvCtrl_BLDC1_Speed_MinSpeedRpsCustom | 20 | 40021 | REAL | holding | 300 | - { address: 20, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Min speed", unique_id: "apollo.BLDC_Mng_CfgEnvCtrl_BLDC1_Speed_MinSpeedRpsCustom"} | 0.0~99.0
Comp BLDC | Out of envelope alarm timeout | BLDC_Mng.CfgEnvCtrl_BLDC1.CstmEnv_EnvOutMaxT | BLDC_Mng_CfgEnvCtrl_BLDC1_CstmEnv_EnvOutMaxT | 21 | 40022 | INT | holding | 300 | - { address: 21, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Out of envelope alarm timeout", unique_id: "apollo.BLDC_Mng_CfgEnvCtrl_BLDC1_CstmEnv_EnvOutMaxT"} | 0-32000
| Low pressure diff alarm timeout | BLDC_Mng.CfgEnvCtrl_BLDC1.CstmEnv_LowDeltaPAlrmDelay | BLDC_Mng_CfgEnvCtrl_BLDC1_CstmEnv_LowDeltaPAlrmDelay | 22 | 40023 | INT | holding | 300 | - { address: 22, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low pressure diff alarm timeout ", unique_id: "apollo.BLDC_Mng_CfgEnvCtrl_BLDC1_CstmEnv_LowDeltaPAlrmDelay"} | 0-32000
Manual requirements | Manual requirements | PmpMan_Aout | PmpMan_Aout | 23 | 40024 | REAL | holding | 300 | - { address: 23, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Manual requirements", unique_id: "apollo.PmpMan_Aout"} | 0.0~100.0
Manual requirements | Manual requirements | fan_man_out | fan_man_out | 24 | 40025 | REAL | holding | 300 | - { address: 24, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Manual requirements", unique_id: "apollo.fan_man_out"} | 0.0~100.0
Manual requirements | Manual requirements | ManBLDCPwrReq | ManBLDCPwrReq | 25 | 40026 | REAL | holding | 300 | - { address: 25, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Manual requirements", unique_id: "apollo.ManBLDCPwrReq"} | 0.0~100.0
Manual Steps | Manual Steps | EVD_Manual_Step | EVD_Manual_Step | 26 | 40027 | INT | holding | 300 | - { address: 26, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Manual Steps", unique_id: "apollo.EVD_Manual_Step"} | 0-480
Temperature mode | Temperature mode | Temp_Target_Select | Temp_Target_Select | 27 | 40028 | INT | holding | 300 | - { address: 27, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Temperature mode ", unique_id: "apollo.Temp_Target_Select"} | 0~1 | 0: Water inlet temperature; 1: Outlet water temperature;
Protection value of inlet and outlet water temperature difference | Protection value of inlet and outlet water temperature difference | DeltaTempSetP | DeltaTempSetP | 28 | 40029 | REAL | holding | 300 | - { address: 28, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Protection value of inlet and outlet water temperature difference", unique_id: "apollo.DeltaTempSetP"} | 2.0~15.0
Low water temperature protection value | Low water temperature protection value | OutLowTempSetP | OutLowTempSetP | 29 | 40030 | REAL | holding | 300 | - { address: 29, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low water temperature protection value", unique_id: "apollo.OutLowTempSetP"} | -99.0~99.0
High water temperature protection value | High water temperature protection value | OutHiTempSetP | OutHiTempSetP | 30 | 40031 | REAL | holding | 300 | - { address: 30, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High water temperature protection value", unique_id: "apollo.OutHiTempSetP"} | -99.0~99.0
Delay after startup | S | threevlv_delayon | threevlv_delayon | 31 | 40032 | INT | holding | 300 | - { address: 31, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - S", unique_id: "apollo.threevlv_delayon"} | 0-999
Delay before stopping | S | threevlv_delayoff | threevlv_delayoff | 32 | 40033 | INT | holding | 300 | - { address: 32, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - S", unique_id: "apollo.threevlv_delayoff"} | 0-999
Starting speed of three-way valve |  | PmpSpeedStart | PmpSpeedStart | 33 | 40034 | REAL | holding | 300 | - { address: 33, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - ", unique_id: "apollo.PmpSpeedStart"} | 0.0~100.0
Three way valve start delay | min | DT_PmpStart | DT_PmpStart | 34 | 40035 | INT | holding | 300 | - { address: 34, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - min", unique_id: "apollo.DT_PmpStart"} | 0-999
Maximum speed | Maximum speed | PmpMaxSpeed | PmpMaxSpeed | 35 | 40036 | REAL | holding | 300 | - { address: 35, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.PmpMaxSpeed"} | 0.0~100.0
Minimum speed | Minimum speed | PmpMinSpeed | PmpMinSpeed | 36 | 40037 | REAL | holding | 300 | - { address: 36, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimum speed", unique_id: "apollo.PmpMinSpeed"} | 0.0~100.0
Probe range | Main valve suction pressure min | nputsCheck.MinVal_SuctP | nputsCheck_MinVal_SuctP | 37 | 40038 | REAL | holding | 300 | - { address: 37, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve suction pressure min", unique_id: "apollo.nputsCheck_MinVal_SuctP"} | -99.0~99.0
| Main valve suction pressure max | InputsCheck.MaxVal_SuctP | InputsCheck_MaxVal_SuctP | 38 | 40039 | REAL | holding | 300 | - { address: 38, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve suction pressure max", unique_id: "apollo.InputsCheck_MaxVal_SuctP"} | -99.0~99.0
| Main valve exhaust pressure min | InputsCheck.MinVal_DscgP | InputsCheck_MinVal_DscgP | 39 | 40040 | REAL | holding | 300 | - { address: 39, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve exhaust pressure min", unique_id: "apollo.InputsCheck_MinVal_DscgP"} | -99.0~99.0
| Main valve exhaust pressure max | InputsCheck.MaxVal_DscgP | InputsCheck_MaxVal_DscgP | 40 | 40041 | REAL | holding | 300 | - { address: 40, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve exhaust pressure max", unique_id: "apollo.InputsCheck_MaxVal_DscgP"} | -99.0~99.0
EVI evaporation pressure range | EVI evaporation pressure min | InputsCheck.MinVal_SuctP_EVI | InputsCheck_MinVal_SuctP_EVI | 41 | 40042 | REAL | holding | 300 | - { address: 41, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - EVI evaporation pressure min", unique_id: "apollo.InputsCheck_MinVal_SuctP_EVI"} | -99.0~99.0
| EVI evaporation pressure max | InputsCheck.MaxVal_SuctP_EVI | InputsCheck_MaxVal_SuctP_EVI | 42 | 40043 | REAL | holding | 300 | - { address: 42, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - EVI evaporation pressure max", unique_id: "apollo.InputsCheck_MaxVal_SuctP_EVI"} | -99.0~99.0
Starting conditions for jet enthalpy increase | Compressor speed | VapInjRotSpeedSe | VapInjRotSpeedSe | 43 | 40044 | REAL | holding | 300 | - { address: 43, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Compressor speed", unique_id: "apollo.VapInjRotSpeedSe"} | 0.0~999.0
| Exhaust superheat setting point | VapInjDischSHSet | VapInjDischSHSet | 44 | 40045 | REAL | holding | 300 | - { address: 44, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Exhaust superheat setting point", unique_id: "apollo.VapInjDischSHSet"} | 0.0~999.0
| Exhaust superheat deviation | VapInjDischSHDiff | VapInjDischSHDiff | 45 | 40046 | REAL | holding | 300 | - { address: 45, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Exhaust superheat deviation", unique_id: "apollo.VapInjDischSHDiff"} | 0.0~999.0
Starting conditions for jet enthalpy increase/cooling | Ambient temp setup | VapInjTExtSetCH | VapInjTExtSetCH | 46 | 40047 | REAL | holding | 300 | - { address: 46, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Ambient temp setup", unique_id: "apollo.VapInjTExtSetCH"} | -999.0~999.0
| Ambient temp deviation | VapInjTExtDiffCH | VapInjTExtDiffCH | 47 | 40048 | REAL | holding | 300 | - { address: 47, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Ambient temp deviation", unique_id: "apollo.VapInjTExtDiffCH"} | -999.0~999.0
Starting conditions for jet enthalpy increase/heating | Ambient temp setup | VapInjTExtSetHP | VapInjTExtSetHP | 48 | 40049 | REAL | holding | 300 | - { address: 48, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Ambient temp setup", unique_id: "apollo.VapInjTExtSetHP"} | -999.0~999.0
| Ambient temp deviation | VapInjTExtDiffHP | VapInjTExtDiffHP | 49 | 40050 | REAL | holding | 300 | - { address: 49, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Ambient temp deviation", unique_id: "apollo.VapInjTExtDiffHP"} | -999.0~999.0
Minimum demand | Minimum demand | OilRecovMinReqThrsh | OilRecovMinReqThrsh | 50 | 40051 | REAL | holding | 300 | - { address: 50, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimum demand", unique_id: "apollo.OilRecovMinReqThrsh"} | 0.0~99.0
Minimum speed | Minimum speed | OilRecovCompMinSpeedThrsh_rps | OilRecovCompMinSpeedThrsh_rps | 51 | 40052 | REAL | holding | 300 | - { address: 51, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimum speed", unique_id: "apollo.OilRecovCompMinSpeedThrsh_rps"} | 0.0~99.0
Detection delay | Detection delay | OilRecovWaitT_min | OilRecovWaitT_min | 52 | 40053 | INT | holding | 300 | - { address: 52, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Detection delay", unique_id: "apollo.OilRecovWaitT_min"} | 10~999
Return oil speed | Return oil speed | OilRecovFrcCompSpeed_rps | OilRecovFrcCompSpeed_rps | 53 | 40054 | REAL | holding | 300 | - { address: 53, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Return oil speed", unique_id: "apollo.OilRecovFrcCompSpeed_rps"} | 0.0~200.0
Oil return time | Oil return time | OilRecovFrcSpeedT_min | OilRecovFrcSpeedT_min | 54 | 40055 | INT | holding | 300 | - { address: 54, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Oil return time", unique_id: "apollo.OilRecovFrcSpeedT_min"} | 1~99
Maximum speed for oil return and defrosting | Maximum speed for oil return and defrosting | oil_defrost_maxspeed | oil_defrost_maxspeed | 55 | 40056 | REAL | holding | 300 | - { address: 55, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed for oil return and defrosting", unique_id: "apollo.oil_defrost_maxspeed"} | 0.0~120.0
Low wind ambient temperature setting point | Low wind ambient temperature setting point | lowfan_amTset | lowfan_amTset | 56 | 40057 | REAL | holding | 300 | - { address: 56, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low wind ambient temperature setting point", unique_id: "apollo.lowfan_amTset"} | 0.0~999.0
High air ambient temperature return difference | High air ambient temperature return difference | lowfan_amTsetdiff | lowfan_amTsetdiff | 57 | 40058 | REAL | holding | 300 | - { address: 57, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High air ambient temperature return difference", unique_id: "apollo.lowfan_amTsetdiff"} | 0.0~999.0
cooling mode fan pressure mode | High pressure setting point | set_highpress | set_highpress | 58 | 40059 | REAL | holding | 300 | - { address: 58, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High pressure setting point", unique_id: "apollo.set_highpress"} | 0.0~99.0
| Open loop difference | set_highpress_diff | set_highpress_diff | 59 | 40060 | REAL | holding | 300 | - { address: 59, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Open loop difference", unique_id: "apollo.set_highpress_diff"} | 0.0~99.0
| Closing return difference | set_highP_Stop_diff | set_highP_Stop_diff | 60 | 40061 | REAL | holding | 300 | - { address: 60, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Closing return difference", unique_id: "apollo.set_highP_Stop_diff"} | 0.0~99.0
heating mode fan pressure mode | Low pressure setting point | set_lowpress | set_lowpress | 61 | 40062 | REAL | holding | 300 | - { address: 61, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low pressure setting point", unique_id: "apollo.set_lowpress"} | 0.0~99.0
| Open loop difference | set_lowpress_diff | set_lowpress_diff | 62 | 40063 | REAL | holding | 300 | - { address: 62, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Open loop difference", unique_id: "apollo.set_lowpress_diff"} | 0.0~99.0
| Closing return difference | set_lowP_Stop_diff | set_lowP_Stop_diff | 63 | 40064 | REAL | holding | 300 | - { address: 63, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Closing return difference", unique_id: "apollo.set_lowP_Stop_diff"} | 0.0~99.0
address | address | CondenserFan.FAN_address | CondenserFan_FAN_address | 64 | 40065 | UDINT | holding | 300 | - { address: 64, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - address", unique_id: "apollo.CondenserFan_FAN_address"} | 0-999
Minimum speed of speed regulating fan | Minimum speed of speed regulating fan | CondenserFan.FAN_min_rpm | CondenserFan_FAN_min_rpm | 66 | 40067 | REAL | holding | 300 | - { address: 66, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimum speed of speed regulating fan", unique_id: "apollo.CondenserFan_FAN_min_rpm"} | 0.0~9999.0
Maximum speed of speed regulating fan | Maximum speed of speed regulating fan | CondenserFan.FAN_max_rpm | CondenserFan_FAN_max_rpm | 67 | 40068 | REAL | holding | 300 | - { address: 67, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed of speed regulating fan", unique_id: "apollo.CondenserFan_FAN_max_rpm"} | 0.0~9999.0
Alarm deviation | Alarm deviation | CondenserFan.fan_RPM_diff_error | CondenserFan_fan_RPM_diff_error | 68 | 40069 | real | holding | 300 | - { address: 68, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Alarm deviation", unique_id: "apollo.CondenserFan_fan_RPM_diff_error"} | 0.0~9999.0
Alarm delay | Alarm delay | CondenserFan.fan_RPM_error_delay | CondenserFan_fan_RPM_error_delay | 69 | 40070 | int | holding | 300 | - { address: 69, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Alarm delay ", unique_id: "apollo.CondenserFan_fan_RPM_error_delay"} | 0~999
Minimum fan speed | Minimum fan speed | min_y1_out | min_y1_out | 70 | 40071 | real | holding | 300 | - { address: 70, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimum fan speed", unique_id: "apollo.min_y1_out"} | 0.0~100.0
Maximum fan speed | Maximum fan speed | max_y1_out | max_y1_out | 71 | 40072 | real | holding | 300 | - { address: 71, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum fan speed", unique_id: "apollo.max_y1_out"} | 0.0~100.0
Lowest set point for refrigeration | Lowest set point for refrigeration | CoolHeatMng.cool_set_min | CoolHeatMng_cool_set_min | 72 | 40073 | real | holding | 300 | - { address: 72, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Lowest set point for refrigeration", unique_id: "apollo.CoolHeatMng_cool_set_min"} | -99~100
Heating highest setting point | Heating highest setting point | CoolHeatMng.heat_set_max | CoolHeatMng_heat_set_max | 73 | 40074 | real | holding | 300 | - { address: 73, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Heating highest setting point", unique_id: "apollo.CoolHeatMng_heat_set_max"} | -99~100
address | address | Protocol.BMS2_Address | Protocol_BMS2_Address | 74 | 40075 | udint | holding | 300 | - { address: 74, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - address", unique_id: "apollo.Protocol_BMS2_Address"} | 1-207
Set a new password | Set a new password | GeneralMng.PwdManuf | GeneralMng_PwdManuf | 76 | 40077 | Uint | holding | 300 | - { address: 76, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Set a new password", unique_id: "apollo.GeneralMng_PwdManuf"} | 0~9999
Minimum speed during defrosting switching | Minimum speed during defrosting switching | RevVlvSpeedRps | RevVlvSpeedRps | 77 | 40078 | REAL | holding | 300 | - { address: 77, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimum speed during defrosting switching", unique_id: "apollo.RevVlvSpeedRps"} | 30.0~90.0
Defrosting EEV opening | Defrosting EEV opening | EVD_DfrStep | EVD_DfrStep | 78 | 40079 | INT | holding | 300 | - { address: 78, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Defrosting EEV opening", unique_id: "apollo.EVD_DfrStep"} | 0-480
Defrosting exit EEV manual opening | Defrosting exit EEV manual opening | EVD_DfrStep2 | EVD_DfrStep2 | 79 | 40080 | INT | holding | 300 | - { address: 79, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Defrosting exit EEV manual opening", unique_id: "apollo.EVD_DfrStep2"} | 0-480
EEV manual running time | EEV manual running time | EVD_DfrStep2_Time | EVD_DfrStep2_Time | 80 | 40081 | INT | holding | 300 | - { address: 80, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - EEV manual running time", unique_id: "apollo.EVD_DfrStep2_Time"} | 0~999
Defrosting compressor speed | Defrosting compressor speed | DfrRunCompPwr | DfrRunCompPwr | 81 | 40082 | REAL | holding | 300 | - { address: 81, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Defrosting compressor speed", unique_id: "apollo.DfrRunCompPwr"} | 30.0~oil_defrost_maxspeed（oil_defrost_maxspeed范围0.0~120.0）
Speed of defrosting main water pump | Speed of defrosting main water pump | DfrPmpSpeed | DfrPmpSpeed | 82 | 40083 | REAL | holding | 300 | - { address: 82, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Speed of defrosting main water pump", unique_id: "apollo.DfrPmpSpeed"} | 0.0~100.0
Defrost entry point | Defrost entry point | DefrostCoreMng.DfrStartThrsh | DefrostCoreMng_DfrStartThrsh | 83 | 40084 | REAL | holding | 300 | - { address: 83, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Defrost entry point", unique_id: "apollo.DefrostCoreMng_DfrStartThrsh"} | -20.0~30.0
Defrost end setting point | Defrost end setting point | DefrostCoreMng.DfrEndThrsh | DefrostCoreMng_DfrEndThrsh | 84 | 40085 | REAL | holding | 300 | - { address: 84, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Defrost end setting point", unique_id: "apollo.DefrostCoreMng_DfrEndThrsh"} | 0.0~30.0
Environmental temperature setting point | Environmental temperature setting point | DefrostCoreMng.AmbTempSetP | DefrostCoreMng_AmbTempSetP | 85 | 40086 | REAL | holding | 300 | - { address: 85, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Environmental temperature setting point", unique_id: "apollo.DefrostCoreMng_AmbTempSetP"} | -30.0~30.0
Defrosting environment and coil temperature difference | Defrosting environment and coil temperature difference | DefrostCoreMng.DfrStartThrsh_DeltaT | DefrostCoreMng_DfrStartThrsh_DeltaT | 86 | 40087 | REAL | holding | 300 | - { address: 86, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Defrosting environment and coil temperature difference", unique_id: "apollo.DefrostCoreMng_DfrStartThrsh_DeltaT"} | 1.0~30.0
Defrost entry delay | Defrost entry delay | DefrostCoreMng.DfrStartDT | DefrostCoreMng_DfrStartDT | 87 | 40088 | UINT | holding | 300 | - { address: 87, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Defrost entry delay", unique_id: "apollo.DefrostCoreMng_DfrStartDT"} | 0~90
Minimize frost time | Minimize frost time | DefrostCoreMng.MinT_DFC | DefrostCoreMng_MinT_DFC | 88 | 40089 | UINT | holding | 300 | - { address: 88, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimize frost time", unique_id: "apollo.DefrostCoreMng_MinT_DFC"} | 1-99
Maximum frost time | Maximum frost time | DefrostCoreMng.MaxT_DFC | DefrostCoreMng_MaxT_DFC | 89 | 40090 | UINT | holding | 300 | - { address: 89, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum frost time", unique_id: "apollo.DefrostCoreMng_MaxT_DFC"} | 1~99
Defrosting interval time | Defrosting interval time | DefrostCoreMng.IntervalT_DFC | DefrostCoreMng_IntervalT_DFC | 90 | 40091 | UINT | holding | 300 | - { address: 90, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Defrosting interval time", unique_id: "apollo.DefrostCoreMng_IntervalT_DFC"} | 0-480
Timed defrosting | Timed defrosting | DefrostCoreMng.Dfr_X_Hrs | DefrostCoreMng_Dfr_X_Hrs | 91 | 40092 | UINT | holding | 300 | - { address: 91, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Timed defrosting", unique_id: "apollo.DefrostCoreMng_Dfr_X_Hrs"} | 1~999
Start defrosting | Start defrosting | DefrostCoreMng.DT_BeforeChgOver_DFC | DefrostCoreMng_DT_BeforeChgOver_DFC | 92 | 40093 | UINT | holding | 300 | - { address: 92, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start defrosting", unique_id: "apollo.DefrostCoreMng_DT_BeforeChgOver_DFC"} | 0~99
End defrosting | End defrosting | DefrostCoreMng.DT_AfterChgOver_DFC | DefrostCoreMng_DT_AfterChgOver_DFC | 93 | 40094 | UINT | holding | 300 | - { address: 93, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - End defrosting", unique_id: "apollo.DefrostCoreMng_DT_AfterChgOver_DFC"} | 0~99
Drip water fan on time | Drip water fan on time | DefrostCoreMng.DripT_DFC | DefrostCoreMng_DripT_DFC | 94 | 40095 | UINT | holding | 300 | - { address: 94, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Drip water fan on time", unique_id: "apollo.DefrostCoreMng_DripT_DFC"} | 0-999
High voltage setting point | High voltage setting point | DefrostCoreMng.Dfr_CondFan_SetP | DefrostCoreMng_Dfr_CondFan_SetP | 95 | 40096 | REAL | holding | 300 | - { address: 95, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High voltage setting point", unique_id: "apollo.DefrostCoreMng_Dfr_CondFan_SetP"} | 0.0~40.0
Return difference | Return difference | DefrostCoreMng.Dfr_CondFan_Diff | DefrostCoreMng_Dfr_CondFan_Diff | 96 | 40097 | REAL | holding | 300 | - { address: 96, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Return difference", unique_id: "apollo.DefrostCoreMng_Dfr_CondFan_Diff"} | 0.0~10.0
High voltage setting point | High voltage setting point | Dfr_DscgP_offset | Dfr_DscgP_offset | 97 | 40098 | REAL | holding | 300 | - { address: 97, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High voltage setting point", unique_id: "apollo.Dfr_DscgP_offset"} | 0.0~40.0
Low voltage setting point | Low voltage setting point | Dfr_SuctP_offset | Dfr_SuctP_offset | 98 | 40099 | REAL | holding | 300 | - { address: 98, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low voltage setting point", unique_id: "apollo.Dfr_SuctP_offset"} | 0.0~30.0
EEV1 MOP protection | Threshold | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.MOP_Thrsh.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_MOP_Thrsh_Val | 99 | 40100 | REAL | holding | 300 | - { address: 99, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Threshold", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_MOP_Thrsh_Val"} | 0.0~999.0
| Integral time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.MOP_Ti.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_MOP_Ti_Val | 100 | 40101 | REAL | holding | 300 | - { address: 100, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Integral time", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_MOP_Ti_Val"} | 0.0~999.0
| Alarm delay | EVD_Emb_1.Params_EVDEMB_1.EVD.Regulation.MOP_AlrmDT.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_Regulation_MOP_AlrmDT_Val | 101 | 40102 | INT | holding | 300 | - { address: 101, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Alarm delay", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_Regulation_MOP_AlrmDT_Val"} | 0~999
EEV1 | Prop.gain | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Kp.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_PID_Kp_Val | 102 | 40103 | REAL | holding | 300 | - { address: 102, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Prop.gain", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_PID_Kp_Val"} | 0.0~999.0
| Integr time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Ti.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_PID_Ti_Val | 103 | 40104 | REAL | holding | 300 | - { address: 103, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Integr time", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_PID_Ti_Val"} | 0.0~3200.0
| Deriv time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Td.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_PID_Td_Val | 104 | 40105 | REAL | holding | 300 | - { address: 104, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Deriv time", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_MainRegulation_PID_Td_Val"} | 0.0~999.0
Minimum EEVI opening when auxiliary valve is closed | Minimum EEVI opening when auxiliary valve is closed | EVD_Emb_1.EVD1_MinSteps | EVD_Emb_1_EVD1_MinSteps | 105 | 40106 | INT | holding | 300 | - { address: 105, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimum EEVI opening when auxiliary valve is closed", unique_id: "apollo.EVD_Emb_1_EVD1_MinSteps"} | 0~480
EEV2 | Prop.gain | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Kp.Val | EVD_Emb_1_2_Params_EVDEMB_1_EVD_MainRegulation_PID_Kp_Val | 106 | 40107 | REAL | holding | 300 | - { address: 106, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Prop.gain", unique_id: "apollo.EVD_Emb_1_2_Params_EVDEMB_1_EVD_MainRegulation_PID_Kp_Val"} | 0.0~999.0
| Integr time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Ti.Val | EVD_Emb_1_2_Params_EVDEMB_1_EVD_MainRegulation_PID_Ti_Val | 107 | 40108 | REAL | holding | 300 | - { address: 107, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Integr time", unique_id: "apollo.EVD_Emb_1_2_Params_EVDEMB_1_EVD_MainRegulation_PID_Ti_Val"} | 0.0~3200.0
| Deriv time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Td.Val | EVD_Emb_1_2_Params_EVDEMB_1_EVD_MainRegulation_PID_Td_Val | 108 | 40109 | REAL | holding | 300 | - { address: 108, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Deriv time", unique_id: "apollo.EVD_Emb_1_2_Params_EVDEMB_1_EVD_MainRegulation_PID_Td_Val"} | 0.0~999.0
EEV2 MOP protection | Threshold | VD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondThrsh.Val | VD_Emb_1_2_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondThrsh_Val | 109 | 40110 | REAL | holding | 300 | - { address: 109, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Threshold", unique_id: "apollo.VD_Emb_1_2_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondThrsh_Val"} | 0.0~999.0
| Integral time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondTi.Val | EVD_Emb_1_2_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondTi_Val | 110 | 40111 | REAL | holding | 300 | - { address: 110, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Integral time", unique_id: "apollo.EVD_Emb_1_2_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondTi_Val"} | 0.0~999.0
| Alarm delay | EVD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondAlrmDT.Val | EVD_Emb_1_2_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondAlrmDT_Val | 111 | 40112 | INT | holding | 300 | - { address: 111, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Alarm delay", unique_id: "apollo.EVD_Emb_1_2_Params_EVDEMB_1_EVD_AuxRegulation_HiTempCondAlrmDT_Val"} | 0-65536
10℃＜ambient temp≤14℃ | Main valve superheat | SH_Set1_User[0] | SH_Set1_User_0 | 112 | 40113 | REAL | holding | 300 | - { address: 112, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_0"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[0] | SH_Set2_User_0 | 113 | 40114 | REAL | holding | 300 | - { address: 113, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_0"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[0] | StartEEV_OpRatio_User_0 | 114 | 40115 | INT | holding | 300 | - { address: 114, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_0"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[0] | EVD_DfrStep_User_0 | 115 | 40116 | INT | holding | 300 | - { address: 115, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_0"} | 0-480
| Maximum speed | MaxSpeedRpsUser[0] | MaxSpeedRpsUser_0 | 116 | 40117 | REAL | holding | 300 | - { address: 116, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_0"} | 0.0~999.0
5℃＜ambient temp≤9℃ | Main valve superheat | SH_Set1_User[1] | SH_Set1_User_1 | 117 | 40118 | REAL | holding | 300 | - { address: 117, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_1"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[1] | SH_Set2_User_1 | 118 | 40119 | REAL | holding | 300 | - { address: 118, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_1"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[1] | StartEEV_OpRatio_User_1 | 119 | 40120 | INT | holding | 300 | - { address: 119, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_1"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[1] | EVD_DfrStep_User_1 | 120 | 40121 | INT | holding | 300 | - { address: 120, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_1"} | 0-480
| Maximum speed | MaxSpeedRpsUser[1] | MaxSpeedRpsUser_1 | 121 | 40122 | REAL | holding | 300 | - { address: 121, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_1"} | 0.0~999.0
0℃＜ambient temp≤4℃ | Main valve superheat | SH_Set1_User[2] | SH_Set1_User_2 | 122 | 40123 | REAL | holding | 300 | - { address: 122, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_2"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[2] | SH_Set2_User_2 | 123 | 40124 | REAL | holding | 300 | - { address: 123, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_2"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[2] | StartEEV_OpRatio_User_2 | 124 | 40125 | INT | holding | 300 | - { address: 124, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_2"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User2] | EVD_DfrStep_User2 | 125 | 40126 | INT | holding | 300 | - { address: 125, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User2"} | 0-480
| Maximum speed | MaxSpeedRpsUser[2] | MaxSpeedRpsUser_2 | 126 | 40127 | REAL | holding | 300 | - { address: 126, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_2"} | 0.0~999.0
一5℃＜ambient temp≤-1℃ | Main valve superheat | SH_Set1_User[3] | SH_Set1_User_3 | 127 | 40128 | REAL | holding | 300 | - { address: 127, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_3"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[3] | SH_Set2_User_3 | 128 | 40129 | REAL | holding | 300 | - { address: 128, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_3"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[3] | StartEEV_OpRatio_User_3 | 129 | 40130 | INT | holding | 300 | - { address: 129, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_3"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[3] | EVD_DfrStep_User_3 | 130 | 40131 | INT | holding | 300 | - { address: 130, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_3"} | 0-480
| Maximum speed | MaxSpeedRpsUser[3] | MaxSpeedRpsUser_3 | 131 | 40132 | REAL | holding | 300 | - { address: 131, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_3"} | 0.0~999.0
一10℃＜ambient temp≤一6℃ | Main valve superheat | SH_Set1_User[4] | SH_Set1_User_4 | 132 | 40133 | REAL | holding | 300 | - { address: 132, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_4"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[4] | SH_Set2_User_4 | 133 | 40134 | REAL | holding | 300 | - { address: 133, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_4"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[4] | StartEEV_OpRatio_User_4 | 134 | 40135 | INT | holding | 300 | - { address: 134, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_4"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[4] | EVD_DfrStep_User_4 | 135 | 40136 | INT | holding | 300 | - { address: 135, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_4"} | 0-480
| Maximum speed | MaxSpeedRpsUser[4] | MaxSpeedRpsUser_4 | 136 | 40137 | REAL | holding | 300 | - { address: 136, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_4"} | 0.0~999.0
—15℃＜ambient temp≤一11℃ | Main valve superheat | SH_Set1_User[5] | SH_Set1_User_5 | 137 | 40138 | REAL | holding | 300 | - { address: 137, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_5"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[5] | SH_Set2_User_5 | 138 | 40139 | REAL | holding | 300 | - { address: 138, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_5"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[5] | StartEEV_OpRatio_User_5 | 139 | 40140 | INT | holding | 300 | - { address: 139, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_5"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[5] | EVD_DfrStep_User_5 | 140 | 40141 | INT | holding | 300 | - { address: 140, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_5"} | 0-480
| Maximum speed | MaxSpeedRpsUser[5] | MaxSpeedRpsUser_5 | 141 | 40142 | REAL | holding | 300 | - { address: 141, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_5"} | 0.0~999.0
一20℃＜ambient temp≤一16℃ | Main valve superheat | SH_Set1_User[6] | SH_Set1_User_6 | 142 | 40143 | REAL | holding | 300 | - { address: 142, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_6"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[6] | SH_Set2_User_6 | 143 | 40144 | REAL | holding | 300 | - { address: 143, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_6"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[6] | StartEEV_OpRatio_User_6 | 144 | 40145 | INT | holding | 300 | - { address: 144, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_6"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[6] | EVD_DfrStep_User_6 | 145 | 40146 | INT | holding | 300 | - { address: 145, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_6"} | 0-480
| Maximum speed | MaxSpeedRpsUser[6] | MaxSpeedRpsUser_6 | 146 | 40147 | REAL | holding | 300 | - { address: 146, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_6"} | 0.0~999.0
ambient temp≤一21℃ | Main valve superheat | SH_Set1_User[7] | SH_Set1_User_7 | 147 | 40148 | REAL | holding | 300 | - { address: 147, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_7"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[7] | SH_Set2_User_7 | 148 | 40149 | REAL | holding | 300 | - { address: 148, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_7"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[7] | StartEEV_OpRatio_User_7 | 149 | 40150 | INT | holding | 300 | - { address: 149, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_7"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[7] | EVD_DfrStep_User_7 | 150 | 40151 | INT | holding | 300 | - { address: 150, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_7"} | 0-480
| Maximum speed | MaxSpeedRpsUser[7] | MaxSpeedRpsUser_7 | 151 | 40152 | REAL | holding | 300 | - { address: 151, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_7"} | 0.0~999.0
15℃＜ambient temp≤24℃ | Main valve superheat | SH_Set1_User[8] | SH_Set1_User_8 | 152 | 40153 | REAL | holding | 300 | - { address: 152, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_8"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[8] | SH_Set2_User_8 | 153 | 40154 | REAL | holding | 300 | - { address: 153, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_8"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[8] | StartEEV_OpRatio_User_8 | 154 | 40155 | INT | holding | 300 | - { address: 154, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_8"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[8] | EVD_DfrStep_User_8 | 155 | 40156 | INT | holding | 300 | - { address: 155, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_8"} | 0-480
| Maximum speed | MaxSpeedRpsUser[8] | MaxSpeedRpsUser_8 | 156 | 40157 | REAL | holding | 300 | - { address: 156, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_8"} | 0.0~999.0
ambient temp＞25℃ | Main valve superheat | SH_Set1_User[9] | SH_Set1_User_9 | 157 | 40158 | REAL | holding | 300 | - { address: 157, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_9"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[9] | SH_Set2_User_9 | 158 | 40159 | REAL | holding | 300 | - { address: 158, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_9"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[9] | StartEEV_OpRatio_User_9 | 159 | 40160 | INT | holding | 300 | - { address: 159, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_9"} | 0~100
| Steps of main valve after defrosting | EVD_DfrStep_User[9] | EVD_DfrStep_User_9 | 160 | 40161 | INT | holding | 300 | - { address: 160, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Steps of main valve after defrosting", unique_id: "apollo.EVD_DfrStep_User_9"} | 0-480
| Maximum speed | MaxSpeedRpsUser[9] | MaxSpeedRpsUser_9 | 161 | 40162 | REAL | holding | 300 | - { address: 161, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_9"} | 0.0~999.0
33℃＜ambient temp≤37℃ | Main valve superheat | SH_Set1_User[10] | SH_Set1_User_10 | 162 | 40163 | REAL | holding | 300 | - { address: 162, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_10"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[10] | SH_Set2_User_10 | 163 | 40164 | REAL | holding | 300 | - { address: 163, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_10"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[10] | StartEEV_OpRatio_User_10 | 164 | 40165 | INT | holding | 300 | - { address: 164, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_10"} | 0~100
| Maximum speed | MaxSpeedRpsUser[10] | MaxSpeedRpsUser_10 | 165 | 40166 | REAL | holding | 300 | - { address: 165, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_10"} | 0.0~999.0
30℃＜ambient temp≤32℃ | Main valve superheat | SH_Set1_User[11] | SH_Set1_User_11 | 166 | 40167 | REAL | holding | 300 | - { address: 166, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_11"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[11] | SH_Set2_User_11 | 167 | 40168 | REAL | holding | 300 | - { address: 167, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_11"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[11] | StartEEV_OpRatio_User_11 | 168 | 40169 | INT | holding | 300 | - { address: 168, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_11"} | 0~100
| Maximum speed | MaxSpeedRpsUser[11] | MaxSpeedRpsUser_11 | 169 | 40170 | REAL | holding | 300 | - { address: 169, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_11"} | 0.0~999.0
26℃＜ambient temp≤29℃ | Main valve superheat | SH_Set1_User[12] | SH_Set1_User_12 | 170 | 40171 | REAL | holding | 300 | - { address: 170, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_12"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[12] | SH_Set2_User_12 | 171 | 40172 | REAL | holding | 300 | - { address: 171, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_12"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[12] | StartEEV_OpRatio_User_12 | 172 | 40173 | INT | holding | 300 | - { address: 172, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_12"} | 0~100
| Maximum speed | MaxSpeedRpsUser[12] | MaxSpeedRpsUser_12 | 173 | 40174 | REAL | holding | 300 | - { address: 173, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_12"} | 0.0~999.0
ambient temp≤25℃ | Main valve superheat | SH_Set1_User[13] | SH_Set1_User_13 | 174 | 40175 | REAL | holding | 300 | - { address: 174, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_13"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[13] | SH_Set2_User_13 | 175 | 40176 | REAL | holding | 300 | - { address: 175, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_13"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[13] | StartEEV_OpRatio_User_13 | 176 | 40177 | INT | holding | 300 | - { address: 176, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_13"} | 0~100
| Maximum speed | MaxSpeedRpsUser[13] | MaxSpeedRpsUser_13 | 177 | 40178 | REAL | holding | 300 | - { address: 177, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_13"} | 0.0~999.0
ambient temp＞38℃ | Main valve superheat | SH_Set1_User[14] | SH_Set1_User_14 | 178 | 40179 | REAL | holding | 300 | - { address: 178, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Main valve superheat", unique_id: "apollo.SH_Set1_User_14"} | -99.0~99.0
| Auxiliary valve superheat | SH_Set2_User[14] | SH_Set2_User_14 | 179 | 40180 | REAL | holding | 300 | - { address: 179, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Auxiliary valve superheat", unique_id: "apollo.SH_Set2_User_14"} | -99.0~99.0
| Start the initial opening of the main valve | StartEEV_OpRatio_User[14] | StartEEV_OpRatio_User_14 | 180 | 40181 | INT | holding | 300 | - { address: 180, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start the initial opening of the main valve", unique_id: "apollo.StartEEV_OpRatio_User_14"} | 0~100
| Maximum speed | MaxSpeedRpsUser[14] | MaxSpeedRpsUser_14 | 181 | 40182 | REAL | holding | 300 | - { address: 181, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Maximum speed", unique_id: "apollo.MaxSpeedRpsUser_14"} | 0.0~999.0
date | year | GeneralMng.YearIn | GeneralMng_YearIn | 182 | 40183 | UINT | holding | 300 | - { address: 182, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - year", unique_id: "apollo.GeneralMng_YearIn"} | 0~99
date | month | GeneralMng.MonthIn | GeneralMng_MonthIn | 183 | 40184 | UINT | holding | 300 | - { address: 183, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - month", unique_id: "apollo.GeneralMng_MonthIn"} | 0~12
date | day | GeneralMng.DayIn | GeneralMng_DayIn | 184 | 40185 | UINT | holding | 300 | - { address: 184, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - day", unique_id: "apollo.GeneralMng_DayIn"} | 0~31
time | Hour | GeneralMng.HourIn | GeneralMng_HourIn | 185 | 40186 | UINT | holding | 300 | - { address: 185, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hour", unique_id: "apollo.GeneralMng_HourIn"} | 0~23
time | branch | GeneralMng.MinuteIn | GeneralMng_MinuteIn | 186 | 40187 | UINT | holding | 300 | - { address: 186, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - branch", unique_id: "apollo.GeneralMng_MinuteIn"} | 0~59
week | week | GeneralMng.DayOfWeek | GeneralMng_DayOfWeek | 187 | 40188 | UINT | holding | 300 | - { address: 187, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - week", unique_id: "apollo.GeneralMng_DayOfWeek"} | 1~7
Return water temperature | Return water temperature | CW_InTemp | CW_InTemp | 188 | 40189 | REAL | holding | 300 | - { address: 188, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Return water temperature", unique_id: "apollo.CW_InTemp"} | ℃/℉
Outlet water temperature | Outlet water temperature | CW_OutTemp | CW_OutTemp | 189 | 40190 | REAL | holding | 300 | - { address: 189, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Outlet water temperature", unique_id: "apollo.CW_OutTemp"} | ℃/℉
Ambient temp | Ambient temp | AmbTemp | AmbTemp | 190 | 40191 | REAL | holding | 300 | - { address: 190, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Ambient temp", unique_id: "apollo.AmbTemp"} | ℃/℉
Exhaust temperature | Exhaust temperature | DscgTemp | DscgTemp | 191 | 40192 | REAL | holding | 300 | - { address: 191, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Exhaust temperature", unique_id: "apollo.DscgTemp"} | ℃/℉
Suction temperature | Suction temperature | SuctTemp | SuctTemp | 192 | 40193 | REAL | holding | 300 | - { address: 192, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Suction temperature", unique_id: "apollo.SuctTemp"} | ℃/℉
High pressure | High pressure | DscgP | DscgP | 193 | 40194 | REAL | holding | 300 | - { address: 193, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High pressure", unique_id: "apollo.DscgP"}
Low pressure | Low pressure | SuctP | SuctP | 194 | 40195 | REAL | holding | 300 | - { address: 194, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low pressure", unique_id: "apollo.SuctP"}
Hot water temperature | Hot water temperature | CW_TankTemp | CW_TankTemp | 195 | 40196 | REAL | holding | 300 | - { address: 195, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hot water temperature", unique_id: "apollo.CW_TankTemp"} | ℃/℉
Coil temperature | Coil temperature | CondsrCoilTemp | CondsrCoilTemp | 196 | 40197 | REAL | holding | 300 | - { address: 196, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Coil temperature", unique_id: "apollo.CondsrCoilTemp"} | ℃/℉
Fan output | Fan output | CondenserFan.y1_out | CondenserFan_y1_out | 197 | 40198 | REAL | holding | 300 | - { address: 197, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Fan output", unique_id: "apollo.CondenserFan_y1_out"}
Water pump output | Water pump output | Pump_Aout | Pump_Aout | 198 | 40199 | REAL | holding | 300 | - { address: 198, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Water pump output", unique_id: "apollo.Pump_Aout"}
Speed regulation fan 1 output | Speed regulation fan 1 output | CondenserFan.fan1_RPM_OUT_2 | CondenserFan_fan1_RPM_OUT_2 | 199 | 40200 | INT | holding | 300 | - { address: 199, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Speed regulation fan 1 output", unique_id: "apollo.CondenserFan_fan1_RPM_OUT_2"}
Speed control fan 1 feedback | Speed control fan 1 feedback | CondenserFan.fan2_RPM_in_2 | CondenserFan_fan2_RPM_in_2 | 200 | 40201 | INT | holding | 300 | - { address: 200, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Speed control fan 1 feedback", unique_id: "apollo.CondenserFan_fan2_RPM_in_2"}
Speed regulation fan 2 output | Speed regulation fan 2 output | CondenserFan.fan2_RPM_OUT_2 | CondenserFan_fan2_RPM_OUT_2 | 201 | 40202 | INT | holding | 300 | - { address: 201, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Speed regulation fan 2 output", unique_id: "apollo.CondenserFan_fan2_RPM_OUT_2"}
Speed control fan 2 feedback | Speed control fan 2 feedback | CondenserFan.fan1_RPM_in_2 | CondenserFan_fan1_RPM_in_2 | 202 | 40203 | INT | holding | 300 | - { address: 202, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Speed control fan 2 feedback", unique_id: "apollo.CondenserFan_fan1_RPM_in_2"}
Required cap | Required cap | BLDC_Mng.Info_BLDC1.Info_CompRequest | BLDC_Mng_Info_BLDC1_Info_CompRequest | 203 | 40204 | REAL | holding | 300 | - { address: 203, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Required cap", unique_id: "apollo.BLDC_Mng_Info_BLDC1_Info_CompRequest"}
Actual cap | Actual cap | BLDC_Mng.Info_BLDC1.Info_ReqSpeedToPWRP | BLDC_Mng_Info_BLDC1_Info_ReqSpeedToPWRP | 204 | 40205 | REAL | holding | 300 | - { address: 204, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Actual cap", unique_id: "apollo.BLDC_Mng_Info_BLDC1_Info_ReqSpeedToPWRP"}
Actual speed | Actual speed | BLDC_Mng.Info_PWRP1.Info_RotorSpeed_rps | BLDC_Mng_Info_PWRP1_Info_RotorSpeed_rps | 205 | 40206 | REAL | holding | 300 | - { address: 205, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Actual speed", unique_id: "apollo.BLDC_Mng_Info_PWRP1_Info_RotorSpeed_rps"}
Evaporation temperature | Evaporation temperature | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH_EvapTemp.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_SH_EvapTemp_Val | 206 | 40207 | REAL | holding | 300 | - { address: 206, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Evaporation temperature", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_SH_EvapTemp_Val"}
Electronic expansion valve opening | Electronic expansion valve opening | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_EEV_PosSteps_Val | 207 | 40208 | INT | holding | 300 | - { address: 207, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Electronic expansion valve opening", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_EEV_PosSteps_Val"}
Discharge Superheat | Discharge Superheat | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.DscgSH.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_DscgSH_Val | 208 | 40209 | REAL | holding | 300 | - { address: 208, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Discharge Superheat ", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_DscgSH_Val"}
Status | Status | BLDC_Mng.Info_BLDC1.Info_HTZone | BLDC_Mng_Info_BLDC1_Info_HTZone | 209 | 40210 | INT | holding | 300 | - { address: 209, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Status", unique_id: "apollo.BLDC_Mng_Info_BLDC1_Info_HTZone"} |  | 0:ok 1:Controlled 2:limited
Protection | Protection | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.ProtStatus.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_ProtStatus_Val | 210 | 40211 | INT | holding | 300 | - { address: 210, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Protection", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_ProtStatus_Val"} |  | 0: none 1：none 2：LowSH 3：lop 4:Mop 5:HiTcond
Suction SH | Suction SH | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH.Val | EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_SH_Val | 211 | 40212 | REAL | holding | 300 | - { address: 211, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Suction SH", unique_id: "apollo.EVD_Emb_1_Params_EVDEMB_1_EVD_Variables_SH_Val"}
Fan shutdown delay | Fan shutdown delay | DT_FanOff | DT_FanOff | 213 | 40214 | INT | holding | 300 | - { address: 213, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Fan shutdown delay", unique_id: "apollo.DT_FanOff"} | 0~60
Antifreeze shutdown delay | Antifreeze shutdown delay | DT_Sysoff_Antif | DT_Sysoff_Antif | 214 | 40215 | INT | holding | 300 | - { address: 214, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Antifreeze shutdown delay", unique_id: "apollo.DT_Sysoff_Antif"} | 0~120
Current operating mode of the unit | Current operating mode of the unit | uniton_mode | uniton_mode | 215 | 40216 | INT | holding | 300 | - { address: 215, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Current operating mode of the unit", unique_id: "apollo.uniton_mode"} |  | 0: cooling 1: Heating 2: Hot water
Current temperature | Current temperature | Temp_Target | Temp_Target | 216 | 40217 | real | holding | 300 | - { address: 216, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Current temperature", unique_id: "apollo.Temp_Target"}
Unit status | Unit status | UnitStatus | UnitStatus | 217 | 40218 | int | holding | 300 | - { address: 217, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Unit status", unique_id: "apollo.UnitStatus"} | 0-11 | 0: Machine preparation; 1: Unit startup; 2: Alarm shutdown; 3: Network shutdown; 4: Monitoring shutdown; 5: Emergency shutdown; 6: Press the button to shut down; 7: Manual mode; 8: Unit antifreeze; 9: Networking switch; 10: Switching off; 11: High-temperature sterilization
Start on Monday: hour | Start on Monday: hour | TimezoneMng.On_Mon_Hour | TimezoneMng_On_Mon_Hour | 218 | 40219 | INT | holding | 300 | - { address: 218, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Monday: hour", unique_id: "apollo.TimezoneMng_On_Mon_Hour"} | 0-23
Start on Monday: minutes | Start on Monday: minutes | TimezoneMng.On_Mon_Min | TimezoneMng_On_Mon_Min | 219 | 40220 | INT | holding | 300 | - { address: 219, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Monday: minutes", unique_id: "apollo.TimezoneMng_On_Mon_Min"} | 0-59
On Tuesday: hour | On Tuesday: hour | TimezoneMng.On_Tue_Hour | TimezoneMng_On_Tue_Hour | 220 | 40221 | INT | holding | 300 | - { address: 220, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - On Tuesday: hour", unique_id: "apollo.TimezoneMng_On_Tue_Hour"} | 0-23
Starting on Tuesday: minutes | Starting on Tuesday: minutes | TimezoneMng.On_Tue_Min | TimezoneMng_On_Tue_Min | 221 | 40222 | INT | holding | 300 | - { address: 221, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Starting on Tuesday: minutes", unique_id: "apollo.TimezoneMng_On_Tue_Min"} | 0-59
On Wednesday: hour | On Wednesday: hour | TimezoneMng.On_Wed_Hour | TimezoneMng_On_Wed_Hour | 222 | 40223 | INT | holding | 300 | - { address: 222, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - On Wednesday: hour", unique_id: "apollo.TimezoneMng_On_Wed_Hour"} | 0-23
Starting on Wednesday: minutes | Starting on Wednesday: minutes | TimezoneMng.On_Wed_Min | TimezoneMng_On_Wed_Min | 223 | 40224 | INT | holding | 300 | - { address: 223, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Starting on Wednesday: minutes", unique_id: "apollo.TimezoneMng_On_Wed_Min"} | 0-59
Start on Thursday: hour | Start on Thursday: hour | TimezoneMng.On_Thu_Hour | TimezoneMng_On_Thu_Hour | 224 | 40225 | INT | holding | 300 | - { address: 224, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Thursday: hour", unique_id: "apollo.TimezoneMng_On_Thu_Hour"} | 0-23
Start on Thursday: minutes | Start on Thursday: minutes | TimezoneMng.On_Thu_Min | TimezoneMng_On_Thu_Min | 225 | 40226 | INT | holding | 300 | - { address: 225, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Thursday: minutes", unique_id: "apollo.TimezoneMng_On_Thu_Min"} | 0-59
Start on Friday: hour | Start on Friday: hour | TimezoneMng.On_Fri_Hour | TimezoneMng_On_Fri_Hour | 226 | 40227 | INT | holding | 300 | - { address: 226, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Friday: hour", unique_id: "apollo.TimezoneMng_On_Fri_Hour"} | 0-23
Start on Friday: minutes | Start on Friday: minutes | TimezoneMng.On_Fri_Min | TimezoneMng_On_Fri_Min | 227 | 40228 | INT | holding | 300 | - { address: 227, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Friday: minutes", unique_id: "apollo.TimezoneMng_On_Fri_Min"} | 0-59
Start on Saturday: hour | Start on Saturday: hour | TimezoneMng.On_Sat_Hour | TimezoneMng_On_Sat_Hour | 228 | 40229 | INT | holding | 300 | - { address: 228, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Saturday: hour", unique_id: "apollo.TimezoneMng_On_Sat_Hour"} | 0-23
Start on Saturday: minutes | Start on Saturday: minutes | TimezoneMng.On_Sat_Min | TimezoneMng_On_Sat_Min | 229 | 40230 | INT | holding | 300 | - { address: 229, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Saturday: minutes", unique_id: "apollo.TimezoneMng_On_Sat_Min"} | 0-59
Start on Sunday: hour | Start on Sunday: hour | TimezoneMng.On_Sun_Hour | TimezoneMng_On_Sun_Hour | 230 | 40231 | INT | holding | 300 | - { address: 230, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Sunday: hour", unique_id: "apollo.TimezoneMng_On_Sun_Hour"} | 0-23
Start on Sunday: minutes | Start on Sunday: minutes | TimezoneMng.On_Sun_Min | TimezoneMng_On_Sun_Min | 231 | 40232 | INT | holding | 300 | - { address: 231, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Start on Sunday: minutes", unique_id: "apollo.TimezoneMng_On_Sun_Min"} | 0-59
Shutdown on Monday: hours | Shutdown on Monday: hours | TimezoneMng.Off_Mon_Hour | TimezoneMng_Off_Mon_Hour | 232 | 40233 | INT | holding | 300 | - { address: 232, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Monday: hours", unique_id: "apollo.TimezoneMng_Off_Mon_Hour"} | 0-23
Shutdown on Monday: minutes | Shutdown on Monday: minutes | TimezoneMng.Off_Mon_Min | TimezoneMng_Off_Mon_Min | 233 | 40234 | INT | holding | 300 | - { address: 233, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Monday: minutes", unique_id: "apollo.TimezoneMng_Off_Mon_Min"} | 0-59
Shutdown on Tuesday: hour | Shutdown on Tuesday: hour | TimezOffeMng.Off_Tue_Hour | TimezOffeMng_Off_Tue_Hour | 234 | 40235 | INT | holding | 300 | - { address: 234, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Tuesday: hour", unique_id: "apollo.TimezOffeMng_Off_Tue_Hour"} | 0-23
Shutdown on Tuesday: minutes | Shutdown on Tuesday: minutes | TimezOffeMng.Off_Tue_Min | TimezOffeMng_Off_Tue_Min | 235 | 40236 | INT | holding | 300 | - { address: 235, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Tuesday: minutes", unique_id: "apollo.TimezOffeMng_Off_Tue_Min"} | 0-59
Shutdown on Wednesday: hour | Shutdown on Wednesday: hour | TimezOffeMng.Off_Wed_Hour | TimezOffeMng_Off_Wed_Hour | 236 | 40237 | INT | holding | 300 | - { address: 236, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Wednesday: hour", unique_id: "apollo.TimezOffeMng_Off_Wed_Hour"} | 0-23
Shutdown on Wednesday: minutes | Shutdown on Wednesday: minutes | TimezOffeMng.Off_Wed_Min | TimezOffeMng_Off_Wed_Min | 237 | 40238 | INT | holding | 300 | - { address: 237, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Wednesday: minutes", unique_id: "apollo.TimezOffeMng_Off_Wed_Min"} | 0-59
Shutdown on Thursday: hour | Shutdown on Thursday: hour | TimezOffeMng.Off_Thu_Hour | TimezOffeMng_Off_Thu_Hour | 238 | 40239 | INT | holding | 300 | - { address: 238, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Thursday: hour", unique_id: "apollo.TimezOffeMng_Off_Thu_Hour"} | 0-23
Shutdown on Thursday: minutes | Shutdown on Thursday: minutes | TimezOffeMng.Off_Thu_Min | TimezOffeMng_Off_Thu_Min | 239 | 40240 | INT | holding | 300 | - { address: 239, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Thursday: minutes", unique_id: "apollo.TimezOffeMng_Off_Thu_Min"} | 0-59
Shutdown on Friday: hour | Shutdown on Friday: hour | TimezOffeMng.Off_Fri_Hour | TimezOffeMng_Off_Fri_Hour | 240 | 40241 | INT | holding | 300 | - { address: 240, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Friday: hour", unique_id: "apollo.TimezOffeMng_Off_Fri_Hour"} | 0-23
Shutdown on Friday: minutes | Shutdown on Friday: minutes | TimezOffeMng.Off_Fri_Min | TimezOffeMng_Off_Fri_Min | 241 | 40242 | INT | holding | 300 | - { address: 241, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Friday: minutes", unique_id: "apollo.TimezOffeMng_Off_Fri_Min"} | 0-59
Shutdown on Saturday: hour | Shutdown on Saturday: hour | TimezOffeMng.Off_Sat_Hour | TimezOffeMng_Off_Sat_Hour | 242 | 40243 | INT | holding | 300 | - { address: 242, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Saturday: hour", unique_id: "apollo.TimezOffeMng_Off_Sat_Hour"} | 0-23
Shutdown on Saturday: minutes | Shutdown on Saturday: minutes | TimezOffeMng.Off_Sat_Min | TimezOffeMng_Off_Sat_Min | 243 | 40244 | INT | holding | 300 | - { address: 243, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Saturday: minutes", unique_id: "apollo.TimezOffeMng_Off_Sat_Min"} | 0-59
Shutdown on Sunday: hour | Shutdown on Sunday: hour | TimezOffeMng.Off_Sun_Hour | TimezOffeMng_Off_Sun_Hour | 244 | 40245 | INT | holding | 300 | - { address: 244, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Sunday: hour", unique_id: "apollo.TimezOffeMng_Off_Sun_Hour"} | 0-23
Shutdown on Sunday: minutes | Shutdown on Sunday: minutes | TimezOffeMng.Off_Sun_Min | TimezOffeMng_Off_Sun_Min | 245 | 40246 | INT | holding | 300 | - { address: 245, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Shutdown on Sunday: minutes", unique_id: "apollo.TimezOffeMng_Off_Sun_Min"} | 0-59
Hour | Hour | TimezoneMng.TempHr1 | TimezoneMng_TempHr1 | 246 | 40247 | INT | holding | 300 | - { address: 246, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hour", unique_id: "apollo.TimezoneMng_TempHr1"} | 0-23
branch | branch | TimezoneMng.TempMin1 | TimezoneMng_TempMin1 | 247 | 40248 | INT | holding | 300 | - { address: 247, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - branch", unique_id: "apollo.TimezoneMng_TempMin1"} | 0-59
refrigeration | refrigeration | TimezoneMng.S_Set_Temp1 | TimezoneMng_S_Set_Temp1 | 248 | 40249 | REAL | holding | 300 | - { address: 248, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - refrigeration", unique_id: "apollo.TimezoneMng_S_Set_Temp1"} | -99.0~99.0
Heating | Heating | TimezoneMng.W_Set_Temp1 | TimezoneMng_W_Set_Temp1 | 249 | 40250 | REAL | holding | 300 | - { address: 249, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Heating", unique_id: "apollo.TimezoneMng_W_Set_Temp1"} | -99.0~99.0
Hour | Hour | TimezoneMng.TempHr2 | TimezoneMng_TempHr2 | 250 | 40251 | INT | holding | 300 | - { address: 250, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hour", unique_id: "apollo.TimezoneMng_TempHr2"} | 0-95
branch | branch | TimezoneMng.TempMin2 | TimezoneMng_TempMin2 | 251 | 40252 | INT | holding | 300 | - { address: 251, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - branch", unique_id: "apollo.TimezoneMng_TempMin2"} | 0-131
refrigeration | refrigeration | TimezoneMng.S_Set_Temp2 | TimezoneMng_S_Set_Temp2 | 252 | 40253 | REAL | holding | 300 | - { address: 252, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - refrigeration", unique_id: "apollo.TimezoneMng_S_Set_Temp2"} | -99.0~99.0
Heating | Heating | TimezoneMng.W_Set_Temp2 | TimezoneMng_W_Set_Temp2 | 253 | 40254 | REAL | holding | 300 | - { address: 253, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Heating", unique_id: "apollo.TimezoneMng_W_Set_Temp2"} | -99.0~99.0
Hour | Hour | TimezoneMng.TempHr3 | TimezoneMng_TempHr3 | 254 | 40255 | INT | holding | 300 | - { address: 254, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hour", unique_id: "apollo.TimezoneMng_TempHr3"} | 0-167
branch | branch | TimezoneMng.TempMin3 | TimezoneMng_TempMin3 | 255 | 40256 | INT | holding | 300 | - { address: 255, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - branch", unique_id: "apollo.TimezoneMng_TempMin3"} | 0-203
refrigeration | refrigeration | TimezoneMng.S_Set_Temp3 | TimezoneMng_S_Set_Temp3 | 256 | 40257 | REAL | holding | 300 | - { address: 256, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - refrigeration", unique_id: "apollo.TimezoneMng_S_Set_Temp3"} | -99.0~99.0
Heating | Heating | TimezoneMng.W_Set_Temp3 | TimezoneMng_W_Set_Temp3 | 257 | 40258 | REAL | holding | 300 | - { address: 257, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Heating", unique_id: "apollo.TimezoneMng_W_Set_Temp3"} | -99.0~99.0
Hour | Hour | TimezoneMng.TempHr4 | TimezoneMng_TempHr4 | 258 | 40259 | INT | holding | 300 | - { address: 258, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hour", unique_id: "apollo.TimezoneMng_TempHr4"} | 0-239
branch | branch | TimezoneMng.TempMin4 | TimezoneMng_TempMin4 | 259 | 40260 | INT | holding | 300 | - { address: 259, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - branch", unique_id: "apollo.TimezoneMng_TempMin4"} | 0-275
refrigeration | refrigeration | TimezoneMng.S_Set_Temp4 | TimezoneMng_S_Set_Temp4 | 260 | 40261 | REAL | holding | 300 | - { address: 260, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - refrigeration", unique_id: "apollo.TimezoneMng_S_Set_Temp4"} | -99.0~99.0
Heating | Heating | TimezoneMng.W_Set_Temp4 | TimezoneMng_W_Set_Temp4 | 261 | 40262 | REAL | holding | 300 | - { address: 261, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Heating", unique_id: "apollo.TimezoneMng_W_Set_Temp4"} | -99.0~99.0
| EEV2 manual steps | EVI_ManSteps | EVI_ManSteps | 262 | 40263 | int | holding | 300 | - { address: 262, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - EEV2 manual steps", unique_id: "apollo.EVI_ManSteps"} | 0-480
Cooling ambient temperature X-axis setting | X1 | X_CH[1] | X_CH_1 | 276 | 40277 | real | holding | 300 | - { address: 276, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X1", unique_id: "apollo.X_CH_1"} | -99.9~99.9
| X2 | X_CH[2] | X_CH_2 | 277 | 40278 | real | holding | 300 | - { address: 277, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X2", unique_id: "apollo.X_CH_2"} | -99.9~99.9
| X3 | X_CH[3] | X_CH_3 | 278 | 40279 | real | holding | 300 | - { address: 278, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X3", unique_id: "apollo.X_CH_3"} | -99.9~99.9
| X4 | X_CH[4] | X_CH_4 | 279 | 40280 | real | holding | 300 | - { address: 279, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X4", unique_id: "apollo.X_CH_4"} | -99.9~99.9
Heating ambient temperature X-axis setting | X1 | X_Hp[1] | X_Hp_1 | 280 | 40281 | real | holding | 300 | - { address: 280, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X1", unique_id: "apollo.X_Hp_1"} | -99.9~99.9
| X2 | X_Hp[2] | X_Hp_2 | 281 | 40282 | real | holding | 300 | - { address: 281, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X2", unique_id: "apollo.X_Hp_2"} | -99.9~99.9
| X3 | X_Hp[3] | X_Hp_3 | 282 | 40283 | real | holding | 300 | - { address: 282, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X3", unique_id: "apollo.X_Hp_3"} | -99.9~99.9
| X4 | X_Hp[4] | X_Hp_4 | 283 | 40284 | real | holding | 300 | - { address: 283, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X4", unique_id: "apollo.X_Hp_4"} | -99.9~99.9
Hot water ambient temperature X-axis setting | X1 | X_DHW[1] | X_DHW_1 | 284 | 40285 | real | holding | 300 | - { address: 284, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X1", unique_id: "apollo.X_DHW_1"} | -99.9~99.9
| X2 | X_DHW[2] | X_DHW_2 | 285 | 40286 | real | holding | 300 | - { address: 285, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X2", unique_id: "apollo.X_DHW_2"} | -99.9~99.9
| X3 | X_DHW[3] | X_DHW_3 | 286 | 40287 | real | holding | 300 | - { address: 286, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X3", unique_id: "apollo.X_DHW_3"} | -99.9~99.9
| X4 | X_DHW[4] | X_DHW_4 | 287 | 40288 | real | holding | 300 | - { address: 287, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - X4", unique_id: "apollo.X_DHW_4"} | -99.9~99.9
Cooling water temperature Y-axis setting point | Y2 | Y_CH[2] | Y_CH_2 | 288 | 40289 | real | holding | 300 | - { address: 288, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y2", unique_id: "apollo.Y_CH_2"} | -99.9~99.9
| Y3 | Y_CH[3] | Y_CH_3 | 289 | 40290 | real | holding | 300 | - { address: 289, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y3", unique_id: "apollo.Y_CH_3"} | -99.9~99.9
| Y4 | Y_CH[4] | Y_CH_4 | 290 | 40291 | real | holding | 300 | - { address: 290, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y4", unique_id: "apollo.Y_CH_4"} | -99.9~99.9
Heating water temperature Y-axis setting point | Y1 | Y_Hp[1] | Y_Hp_1 | 291 | 40292 | real | holding | 300 | - { address: 291, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y1", unique_id: "apollo.Y_Hp_1"} | -99.9~99.9
| Y2 | Y_Hp[2] | Y_Hp_2 | 292 | 40293 | real | holding | 300 | - { address: 292, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y2", unique_id: "apollo.Y_Hp_2"} | -99.9~99.9
| Y3 | Y_Hp[3] | Y_Hp_3 | 293 | 40294 | real | holding | 300 | - { address: 293, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y3", unique_id: "apollo.Y_Hp_3"} | -99.9~99.9
Hot water temperature Y-axis setting point | Y1 | Y_DHW[1] | Y_DHW_1 | 294 | 40295 | real | holding | 300 | - { address: 294, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y1", unique_id: "apollo.Y_DHW_1"} | -99.9~99.9
| Y2 | Y_DHW[2] | Y_DHW_2 | 295 | 40296 | real | holding | 300 | - { address: 295, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y2", unique_id: "apollo.Y_DHW_2"} | -99.9~99.9
| Y3 | Y_DHW[3] | Y_DHW_3 | 296 | 40297 | real | holding | 300 | - { address: 296, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Y3", unique_id: "apollo.Y_DHW_3"} | -99.9~99.9
| Setting point for environmental temperature switching mode | Amb_switch_SetP | Amb_switch_SetP | 297 | 40298 | real | holding | 300 | - { address: 297, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Setting point for environmental temperature switching mode", unique_id: "apollo.Amb_switch_SetP"} | 10.0~30.0
| Loop temperature switching mode return difference | Amb_switch_Offs | Amb_switch_Offs | 298 | 40299 | real | holding | 300 | - { address: 298, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Loop temperature switching mode return difference", unique_id: "apollo.Amb_switch_Offs"} | 0.0~20.0
| Minimum start interval of water pump | MIN_pumpoffTime | MIN_pumpoffTime | 299 | 40300 | int | holding | 300 | - { address: 299, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Minimum start interval of water pump", unique_id: "apollo.MIN_pumpoffTime"} | 1~99min
| Correction value of return water temperature | CW_InTemp_Offs | CW_InTemp_Offs | 300 | 40301 | real | holding | 300 | - { address: 300, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Correction value of return water temperature", unique_id: "apollo.CW_InTemp_Offs"} | 0.0~99.0
| Correction value of outlet water temperature | CW_OutTemp_Offs | CW_OutTemp_Offs | 301 | 40302 | real | holding | 300 | - { address: 301, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Correction value of outlet water temperature", unique_id: "apollo.CW_OutTemp_Offs"} | 0.0~99.0
| Ambient temp correction value | AmbTemp_Offs | AmbTemp_Offs | 302 | 40303 | real | holding | 300 | - { address: 302, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Ambient temp correction value", unique_id: "apollo.AmbTemp_Offs"} | 0.0~99.0
| Exhaust temperature correction value | DscgTemp_Offs | DscgTemp_Offs | 303 | 40304 | real | holding | 300 | - { address: 303, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Exhaust temperature correction value", unique_id: "apollo.DscgTemp_Offs"} | 0.0~99.0
| Correction value of suction temperature | SuctTemp_Offs | SuctTemp_Offs | 304 | 40305 | real | holding | 300 | - { address: 304, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Correction value of suction temperature", unique_id: "apollo.SuctTemp_Offs"} | 0.0~99.0
| High pressure correction value | DscgP_Offs | DscgP_Offs | 305 | 40306 | real | holding | 300 | - { address: 305, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High pressure correction value", unique_id: "apollo.DscgP_Offs"} | 0.0~99.0
| Low pressure correction value | SuctP_Offs | SuctP_Offs | 306 | 40307 | real | holding | 300 | - { address: 306, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low pressure correction value", unique_id: "apollo.SuctP_Offs"} | 0.0~99.0
| Correction value of hot water temperature | Water_Tank_Temp_Offs | Water_Tank_Temp_Offs | 307 | 40308 | real | holding | 300 | - { address: 307, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Correction value of hot water temperature", unique_id: "apollo.Water_Tank_Temp_Offs"} | 0.0~99.0
| Correction value for coil temperature | CondsrCoilTemp_Offs | CondsrCoilTemp_Offs | 308 | 40309 | real | holding | 300 | - { address: 308, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Correction value for coil temperature", unique_id: "apollo.CondsrCoilTemp_Offs"} | 0.0~99.0
| Electronic expansion valve 2 opening | EVD_Emb_1_2.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | EVD_Emb_1_2_Params_EVDEMB_1_EVD_Variables_EEV_PosSteps_Val | 309 | 40310 | int | holding | 300 | - { address: 309, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Electronic expansion valve 2 opening", unique_id: "apollo.EVD_Emb_1_2_Params_EVDEMB_1_EVD_Variables_EEV_PosSteps_Val"} | 0-480
| High temperature differential load reduction deviation | DeltaTemp_Deload_SetP1 | DeltaTemp_Deload_SetP1 | 310 | 40311 | real | holding | 300 | - { address: 310, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High temperature differential load reduction deviation", unique_id: "apollo.DeltaTemp_Deload_SetP1"} | 0.0-99.0
| High temperature difference frequency limiting deviation | DeltaTemp_Deload_SetP2 | DeltaTemp_Deload_SetP2 | 311 | 40312 | real | holding | 300 | - { address: 311, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High temperature difference frequency limiting deviation", unique_id: "apollo.DeltaTemp_Deload_SetP2"} | 0.0-99.0
| High temperature difference frequency limiting exit deviation | DeltaTemp_Deload_SetP3 | DeltaTemp_Deload_SetP3 | 312 | 40313 | real | holding | 300 | - { address: 312, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High temperature difference frequency limiting exit deviation", unique_id: "apollo.DeltaTemp_Deload_SetP3"} | 0.0-99.0
| Deviation of high water outlet load reduction | OutletHighTemp_Deload_SetP1 | OutletHighTemp_Deload_SetP1 | 313 | 40314 | real | holding | 300 | - { address: 313, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Deviation of high water outlet load reduction", unique_id: "apollo.OutletHighTemp_Deload_SetP1"} | 0.0-99.0
| High water outlet frequency limit deviation | OutletHighTemp_Deload_SetP2 | OutletHighTemp_Deload_SetP2 | 314 | 40315 | real | holding | 300 | - { address: 314, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - High water outlet frequency limit deviation", unique_id: "apollo.OutletHighTemp_Deload_SetP2"} | 0.0-99.0
| Exit deviation of high water outlet frequency limit | OutletHighTemp_Deload_SetP3 | OutletHighTemp_Deload_SetP3 | 315 | 40316 | real | holding | 300 | - { address: 315, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Exit deviation of high water outlet frequency limit", unique_id: "apollo.OutletHighTemp_Deload_SetP3"} | 0.0-99.0
| Deviation of low effluent load reduction | OutletLowTemp_Deload_SetP1 | OutletLowTemp_Deload_SetP1 | 316 | 40317 | real | holding | 300 | - { address: 316, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Deviation of low effluent load reduction", unique_id: "apollo.OutletLowTemp_Deload_SetP1"} | 0.0-99.0
| Low water outlet frequency limit deviation | OutletLowTemp_Deload_SetP2 | OutletLowTemp_Deload_SetP2 | 317 | 40318 | real | holding | 300 | - { address: 317, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low water outlet frequency limit deviation", unique_id: "apollo.OutletLowTemp_Deload_SetP2"} | 0.0-99.0
| Low water outlet frequency limit exit deviation | OutletLowTemp_Deload_SetP3 | OutletLowTemp_Deload_SetP3 | 318 | 40319 | real | holding | 300 | - { address: 318, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Low water outlet frequency limit exit deviation", unique_id: "apollo.OutletLowTemp_Deload_SetP3"} | 0.0-99.0
| Frequency reduction delay | Deloading_delay | Deloading_delay | 319 | 40320 | int | holding | 300 | - { address: 319, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Frequency reduction delay", unique_id: "apollo.Deloading_delay"} | 0-99
| Frequency reduction status | Deload_Code | Deload_Code | 320 | 40321 | int | holding | 300 | - { address: 320, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Frequency reduction status", unique_id: "apollo.Deload_Code"} | 0: 1: High temperature differential frequency limit 2: Low water outlet frequency limit 3: High water outlet frequency limit
| Frequency reduction interval | Deload_Interval_time | Deload_Interval_time | 321 | 40322 | int | holding | 300 | - { address: 321, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Frequency reduction interval", unique_id: "apollo.Deload_Interval_time"} | Unit: seconds
| Frequency reduction rate | Deload_rate | Deload_rate | 322 | 40323 | real | holding | 300 | - { address: 322, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Frequency reduction rate", unique_id: "apollo.Deload_rate"}
| Electric heating modes | Aux Head Modes | Aux_Head_Modes | 323 | 40324 | INT | holding | 300 | - { address: 323, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Electric heating modes", unique_id: "apollo.Aux_Head_Modes"} | 0: Disabled 1: Hot water 2: Floor heating 3: Shared
| Antifreeze requirements | Anti_CompReq | Anti_CompReq | 324 | 40325 | real | holding | 300 | - { address: 324, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Antifreeze requirements", unique_id: "apollo.Anti_CompReq"}
| Program version number 1 | GeneralMng.CurrVer.X | GeneralMng_CurrVer_X | 325 | 40326 | INT | holding | 300 | - { address: 325, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Program version number 1", unique_id: "apollo.GeneralMng_CurrVer_X"}
| Program version number 2 | GeneralMng.CurrVer.Y | GeneralMng_CurrVer_Y | 326 | 40327 | INT | holding | 300 | - { address: 326, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Program version number 2", unique_id: "apollo.GeneralMng_CurrVer_Y"}
| Program version number 3 | GeneralMng.CurrVer.Z | GeneralMng_CurrVer_Z | 327 | 40328 | INT | holding | 300 | - { address: 327, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Program version number 3", unique_id: "apollo.GeneralMng_CurrVer_Z"}
| Unit Model Code 1 | GeneralMng.UnitType_A | GeneralMng_UnitType_A | 328 | 40329 | INT | holding | 300 | - { address: 328, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Unit Model Code 1", unique_id: "apollo.GeneralMng_UnitType_A"}
| Unit Model Code 2 | GeneralMng.UnitType_B | GeneralMng_UnitType_B | 329 | 40330 | INT | holding | 300 | - { address: 329, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Unit Model Code 2", unique_id: "apollo.GeneralMng_UnitType_B"}
| Delayed start of the water pump for three minutes during fault standby | Alarm_pumpoff_Time | Alarm_pumpoff_Time | 330 | 40331 | int | holding | 300 | - { address: 330, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Delayed start of the water pump for three minutes during fault standby", unique_id: "apollo.Alarm_pumpoff_Time"} | min
| During normal standby, delay starting the water pump for three minutes | Unit_StandBy_Anti_Delay | Unit_StandBy_Anti_Delay | 331 | 40332 | INT | holding | 300 | - { address: 331, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - During normal standby, delay starting the water pump for three minutes", unique_id: "apollo.Unit_StandBy_Anti_Delay"} | min
| Input and output frequency converter default value | BLDC_Mng.MiscMng_PWRP1.Mng_WriteDefault | BLDC_Mng_MiscMng_PWRP1_Mng_WriteDefault | 332 | 40333 | int | holding | 300 | - { address: 332, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Input and output frequency converter default value", unique_id: "apollo.BLDC_Mng_MiscMng_PWRP1_Mng_WriteDefault"} | 0: No 1: Yes
| Frequency converter power | BLDC_Mng.Info_PWRP1.Info_MotPwr | BLDC_Mng_Info_PWRP1_Info_MotPwr | 333 | 40334 | real | holding | 300 | - { address: 333, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Frequency converter power", unique_id: "apollo.BLDC_Mng_Info_PWRP1_Info_MotPwr"}
| Frequency converter voltage | BLDC_Mng.Info_PWRP1.Info_MotV | BLDC_Mng_Info_PWRP1_Info_MotV | 334 | 40335 | int | holding | 300 | - { address: 334, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Frequency converter voltage", unique_id: "apollo.BLDC_Mng_Info_PWRP1_Info_MotV"}
| Frequency converter current | BLDC_Mng.Info_PWRP1.Info_MotA | BLDC_Mng_Info_PWRP1_Info_MotA | 335 | 40336 | real | holding | 300 | - { address: 335, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Frequency converter current", unique_id: "apollo.BLDC_Mng_Info_PWRP1_Info_MotA"}
Heating setting point | Heating setting point F | CFchange.HeatSetP_F | CFchange_HeatSetP_F | 491 | 40492 | REAL | holding | 300 | - { address: 491, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Heating setting point F", unique_id: "apollo.CFchange_HeatSetP_F"} | 50.0~CFchange.heat_set_max_F默认131）范围 | Setpoint ℉ added
Refrigeration setting point | Refrigeration setting point F | CFchange.CoolSetP_F | CFchange_CoolSetP_F | 492 | 40493 | REAL | holding | 300 | - { address: 492, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Refrigeration setting point F", unique_id: "apollo.CFchange_CoolSetP_F"} | CFchange.cool_set_min_F（默认53.6）~104范围 | Setpoint ℉ added
Hot water setting point | Hot water setting point F | CFchange.W_TankSetP_F | CFchange_W_TankSetP_F | 493 | 40494 | REAL | holding | 300 | - { address: 493, scan_interval: 300, input_type: holding, slave: 1, name: "ApolloHP - Hot water setting point F", unique_id: "apollo.CFchange_W_TankSetP_F"} | 50.0~CFchange.heat_set_max_F（默认131）范围 | Setpoint ℉ added

## PID tuning
P | 1
I | 0
D | 0
P | 1
I | 60
D | 0
P | 1
I | 60
D | 60