## Raw
AIR TO WATER HEAT PUMP 220V EVI INVERTER |  |  | variable | index | modbus | default | data type | range | note
User parameter settings（User mask） | Electric heating control |  | En_AuxHeat | 0 | 00001 | 0 | bool |  | 0: Day mode; 1: Night mode; 2: Low wind mode; 3: Pressure mode;
| Crankshaft/chassis electric heating control |  | En_Customer_16 | 1 | 00002 | 1 | bool
| Power-off self start |  | OnOffUnitMng.UnitTypAfterPwrOff | 2 | 00003 | 1 | bool
| Working mode |  | CoolHeat_Mode | 0 | 40001 |  | int | 0~5 | 0: Cooling mode; 1: Heating mode; 2: Hot water mode; 3: Hot water+refrigeration; 4: Hot water+heating; 5: Swimming pool
| Heating setting point |  | HeatSetP | 1 | 40002 |  | REAL | 10.0~CoolHeatMng.heat_set_max默认55 | Set value ℃
| Refrigeration setting point |  | CoolSetP | 2 | 40003 |  | REAL | CoolHeatMng.cool_set_min默认12~40.0 | Set value ℃
| Hot water point setting |  | W_TankSetP | 3 | 40004 |  | REAL | 10.0~CoolHeatMng.heat_set_max默认55 | Set value ℃
| Hot water return difference |  | hotwater_start_diff | 4 | 40005 |  | REAL | 1.0~15.0
| Hot water constant temperature shutdown |  | hotwater_stop_diff | 5 | 40006 |  | REAL | 0.0~5.0
| Cooling and heating return difference |  | Temp_Diff | 6 | 40007 |  | REAL | 1.0~15.0
| Refrigeration heating constant temperature shutdown |  | Stop_TemP_Diff | 7 | 40008 |  | REAL | 0.0~5.0
| deviation |  | Kp | 8 | 40009 |  | REAL | 1.0~999.0
| Integral time |  | Ti | 9 | 40010 |  | UINT | 0-9999
| Differential time |  | Td | 10 | 40011 |  | UINT | 0-9999
| Main engine water pump |  | PmpMode | 11 | 40012 |  | int | 0~1 | 0: on; 1: Based on demand;
| Fan mode |  | FanMode_Sel | 12 | 40013 |  | int | 0~3
| Electric heating start delay |  | DT_AuxComp | 13 | 40014 |  | UINT | 0-999
| Electric heating start temperature |  | AuxHeatSetP_Exterior | 14 | 40015 |  | real | -30.0~20.0
| Main water pump control | Speed control inlet and outlet water temperature difference | PmpDeltaTempSetP | 15 | 40016 |  | real | 2.0~15.0
| Heating setting point |  | CFchange.HeatSetP_F | 491 | 40492 |  | REAL | 50.0~CFchange.heat_set_max_F默认131）范围 | Setpoint ℉ added
| Refrigeration setting point |  | CFchange.CoolSetP_F | 492 | 40493 |  | REAL | CFchange.cool_set_min_F（默认53.6）~104范围 | Setpoint ℉ added
| Hot water setting point |  | CFchange.W_TankSetP_F | 493 | 40494 |  | REAL | 50.0~CFchange.heat_set_max_F（默认131）范围 | Setpoint ℉ added
Configure compressor parameters（ BLDC COMPRESSOR） | Low pressure alarm delay | start delay | StartUpDT_SuctLowP | 16 | 40017 |  | int | 0~999
|  | Operation delay | DT_SuctLowPrun | 17 | 40018 |  | int | 0~999
| Speed management | Start-up forced speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_StartUpSpeed | 18 | 40019 |  | REAL | 20.0~120.0
|  | Max speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_MaxSpeedRpsCustom | 19 | 40020 |  | REAL | 0.0~999.0
|  | Min speed | BLDC_Mng.CfgEnvCtrl_BLDC1.Speed_MinSpeedRpsCustom | 20 | 40021 |  | REAL | 0.0~99.0
| Comp BLDC | Out of envelope alarm timeout | BLDC_Mng.CfgEnvCtrl_BLDC1.CstmEnv_EnvOutMaxT | 21 | 40022 |  | INT | 0-32000
|  | Low pressure diff alarm timeout | BLDC_Mng.CfgEnvCtrl_BLDC1.CstmEnv_LowDeltaPAlrmDelay | 22 | 40023 |  | INT | 0-32000
（Manual Control） | Water pump manual |  | En_PmpMan | 3 | 00004 | 0 | BOOL
| Manual speed control fan |  | fan_man_en | 4 | 00005 | 0 | BOOL
| Compressor manual |  | CompMan | 5 | 00006 | 0 | BOOL
| EEV manual |  | EVD_Manual | 6 | 00007 | 0 | BOOL
| Manual four-way valve |  | ManDout3 | 7 | 00008 | 0 | BOOL
| Manual waterway three-way valve |  | ManDout5 | 8 | 00009 | 0 | BOOL
| Manual crankshaft electric heating |  | ManDout6 | 9 | 00010 | 0 | BOOL
| Manual chassis electric heating |  | ManDout7 | 10 | 00011 | 0 | BOOL
| Manual end pump |  | ManDout8 | 11 | 00012 | 0 | BOOL
| Manual electric heating |  | ManDout9 | 12 | 00013 | 0 | BOOL
| Insert frequency converter parameters |  | Insert_POWER | 13 | 00014 | 0 | BOOL
| Manual requirements |  | PmpMan_Aout | 23 | 40024 |  | REAL | 0.0~100.0
| Manual requirements |  | fan_man_out | 24 | 40025 |  | REAL | 0.0~100.0
| Manual requirements |  | ManBLDCPwrReq | 25 | 40026 |  | REAL | 0.0~100.0
| Manual Steps |  | EVD_Manual_Step | 26 | 40027 |  | INT | 0-480
（OTHER PARAMETERS） | Enable upper machine monitoring |  | BmsOnOff_En | 15 | 00016 | 0 | BOOL
| Unit mode |  | en_three_valve | 42 | 00043 | 0 | BOOL |  | 0: Dual supply 1: Triple supply
| Temperature mode |  | Temp_Target_Select | 27 | 40028 |  | INT | 0~1 | 0: Water inlet temperature; 1: Outlet water temperature;
| Protection value of inlet and outlet water temperature difference |  | DeltaTempSetP | 28 | 40029 |  | REAL | 2.0~15.0
| Low water temperature protection value |  | OutLowTempSetP | 29 | 40030 |  | REAL | -99.0~99.0
| High water temperature protection value |  | OutHiTempSetP | 30 | 40031 |  | REAL | -99.0~99.0
| Delay after startup | S | threevlv_delayon | 31 | 40032 |  | INT | 0-999
| Delay before stopping | S | threevlv_delayoff | 32 | 40033 |  | INT | 0-999
| Starting speed of three-way valve |  | PmpSpeedStart | 33 | 40034 |  | REAL | 0.0~100.0
| Three way valve start delay | min | DT_PmpStart | 34 | 40035 |  | INT | 0-999
| Maximum speed |  | PmpMaxSpeed | 35 | 40036 |  | REAL | 0.0~100.0
| Minimum speed |  | PmpMinSpeed | 36 | 40037 |  | REAL | 0.0~100.0
| normally open/normally closed | ID1: Water flow switch | InputsCheck.FlwSw_Logic | 16 | 00017 | 0 | BOOL
|  | ID2: Emergency switch | InputsCheck.RemoteOnOff_Logic | 17 | 00018 | 0 | BOOL
|  | ID3: End signal switch | InputsCheck.Terminal_Switch_Logic | 18 | 00019 | 1 | BOOL
|  | ID5: power phase | InputsCheck.ProtSeqPh_Logic | 19 | 00020 | 0 | BOOL
|  | DO1: High wind | Outputs.FanHiSpeed_Logic | 20 | 00021 | 0 | BOOL
|  | DO2: Low wind | Outputs.FanHiSpeed_Logic | 21 | 00022 | 1 | BOOL
|  | DO3: Four way valve | FwVlv_On_Logic | 22 | 00023 | 0 | BOOL
|  | DO4: Host water pump | Outputs.Pmp_On_Logic | 23 | 00024 | 0 | BOOL
|  | DO5: Waterway three-way valve | Outputs.ThreeWVlv_Logic | 24 | 00025 | 0 | BOOL
|  | DO6: Electric heating of crankshaft | Outputs.HeatCrack_Logic | 25 | 00026 | 0 | BOOL
|  | DO7: Chassis electric heating | Outputs.Heat_Chassis_Logic | 26 | 00027 | 0 | BOOL
|  | DO8: End pump | Outputs.Terminal_Pump_Logic | 27 | 00028 | 0 | BOOL
|  | DO9: Electric heating | Outputs.AuxHeat_Logic | 28 | 00029 | 1 | BOOL
| Probe range | Main valve suction pressure range | nputsCheck.MinVal_SuctP | 37 | 40038 |  | REAL | -99.0~99.0
|  |  | InputsCheck.MaxVal_SuctP | 38 | 40039 |  | REAL | -99.0~99.0
|  | Main valve exhaust pressure range | InputsCheck.MinVal_DscgP | 39 | 40040 |  | REAL | -99.0~99.0
|  |  | InputsCheck.MaxVal_DscgP | 40 | 40041 |  | REAL | -99.0~99.0
| Auxiliary electronic expansion valve |  | EnVaporInj | 30 | 00031 | 1 | BOOL
| Enthalpy increasing valve control mode |  | EEV2_control_mode | 29 | 00030 | 1 | BOOL |  | 0: Inhalation superheat; 1: Exhaust superheat;
| EVI evaporation pressure range | Min | InputsCheck.MinVal_SuctP_EVI | 41 | 40042 |  | REAL | -99.0~99.0
|  | Max | InputsCheck.MaxVal_SuctP_EVI | 42 | 40043 |  | REAL | -99.0~99.0
| Starting conditions for jet enthalpy increase | Compressor speed | VapInjRotSpeedSe | 43 | 40044 |  | REAL | 0.0~999.0
|  | Exhaust superheat setting point | VapInjDischSHSet | 44 | 40045 |  | REAL | 0.0~999.0
|  | Exhaust superheat deviation | VapInjDischSHDiff | 45 | 40046 |  | REAL | 0.0~999.0
| Starting conditions for jet enthalpy increase/cooling | Ambient temp setup | VapInjTExtSetCH | 46 | 40047 |  | REAL | -999.0~999.0
|  | Ambient temp deviation | VapInjTExtDiffCH | 47 | 40048 |  | REAL | -999.0~999.0
| Starting conditions for jet enthalpy increase/heating | Ambient temp setup | VapInjTExtSetHP | 48 | 40049 |  | REAL | -999.0~999.0
|  | Ambient temp deviation | VapInjTExtDiffHP | 49 | 40050 |  | REAL | -999.0~999.0
| Fan shutdown delay | S | DT_FanOff | 213 | 40214 |  | INT | 0~60
| Antifreeze shutdown delay | min | DT_Sysoff_Antif | 214 | 40215 |  | INT | 0~120
| Enable return oil control |  | En_OilRecov | 31 | 00032 | 1 | BOOL
| Minimum demand |  | OilRecovMinReqThrsh | 50 | 40051 |  | REAL | 0.0~99.0
| Minimum speed |  | OilRecovCompMinSpeedThrsh_rps | 51 | 40052 |  | REAL | 0.0~99.0
| Detection delay |  | OilRecovWaitT_min | 52 | 40053 |  | INT | 10~999
| Return oil speed |  | OilRecovFrcCompSpeed_rps | 53 | 40054 |  | REAL | 0.0~200.0
| Oil return time |  | OilRecovFrcSpeedT_min | 54 | 40055 |  | INT | 1~99
| Maximum speed for oil return and defrosting |  | oil_defrost_maxspeed | 55 | 40056 |  | REAL | 0.0~120.0
| Low wind ambient temperature setting point |  | lowfan_amTset | 56 | 40057 |  | REAL | 0.0~999.0
| High air ambient temperature return difference |  | lowfan_amTsetdiff | 57 | 40058 |  | REAL | 0.0~999.0
| cooling mode fan pressure mode | High pressure setting point | set_highpress | 58 | 40059 |  | REAL | 0.0~99.0
|  | Open loop difference | set_highpress_diff | 59 | 40060 |  | REAL | 0.0~99.0
|  | Closing return difference | set_highP_Stop_diff | 60 | 40061 |  | REAL | 0.0~99.0
| heating mode fan pressure mode | Low pressure setting point | set_lowpress | 61 | 40062 |  | REAL | 0.0~99.0
|  | Open loop difference | set_lowpress_diff | 62 | 40063 |  | REAL | 0.0~99.0
|  | Closing return difference | set_lowP_Stop_diff | 63 | 40064 |  | REAL | 0.0~99.0
| address |  | CondenserFan.FAN_address | 64 | 40065 |  | UDINT | 0-999
| Minimum speed of speed regulating fan |  | CondenserFan.FAN_min_rpm | 66 | 40067 |  | REAL | 0.0~9999.0
| Maximum speed of speed regulating fan |  | CondenserFan.FAN_max_rpm | 67 | 40068 |  | REAL | 0.0~9999.0
| Speed control fan activation |  | CondenserFan.en_fan_rpm | 32 | 00033 | 0 | bool
| Alarm deviation |  | CondenserFan.fan_RPM_diff_error | 68 | 40069 |  | real | 0.0~9999.0
| Alarm delay |  | CondenserFan.fan_RPM_error_delay | 69 | 40070 |  | int | 0~999
| Fan communication failure shutdown |  | en_al_fan_offcom | 33 | 00034 | 0 | bool
| Minimum fan speed |  | min_y1_out | 70 | 40071 |  | real | 0.0~100.0
| Maximum fan speed |  | max_y1_out | 71 | 40072 |  | real | 0.0~100.0
| Lowest set point for refrigeration |  | CoolHeatMng.cool_set_min | 72 | 40073 |  | real | -99~100
| Heating highest setting point |  | CoolHeatMng.heat_set_max | 73 | 40074 |  | real | -99~100
| address |  | Protocol.BMS2_Address | 74 | 40075 |  | udint | 1-207
| Enable networking |  | En_NetWork | 34 | 00035 | 0 | bool
| Set Unit Category |  | DevicesRotation_mng.MB_Choise | 35 | 00036 | 0 | bool |  | 0: Slave; 1: Host;
| Set a new password |  | GeneralMng.PwdManuf | 76 | 40077 |  | Uint | 0~9999
| language | [7 empty] | No such variable
（defrost） | Enable defrosting |  | En_DefrostMng | 36 | 00037 | 1 | BOOL
| Defrost switching four-way valve press compensation |  | En_Dfr_PressOffset | 37 | 00038 | 1 | BOOL
| Minimum speed during defrosting switching |  | RevVlvSpeedRps | 77 | 40078 |  | REAL | 30.0~90.0
| Defrosting EEV opening |  | EVD_DfrStep | 78 | 40079 |  | INT | 0-480
| Defrosting exit EEV manual opening |  | EVD_DfrStep2 | 79 | 40080 |  | INT | 0-480
| EEV manual running time |  | EVD_DfrStep2_Time | 80 | 40081 |  | INT | 0~999
| Defrosting compressor speed |  | DfrRunCompPwr | 81 | 40082 |  | REAL | 30.0~oil_defrost_maxspeed（oil_defrost_maxspeed范围0.0~120.0）
| Speed of defrosting main water pump |  | DfrPmpSpeed | 82 | 40083 |  | REAL | 0.0~100.0
| Defrost entry point |  | DefrostCoreMng.DfrStartThrsh | 83 | 40084 |  | REAL | -20.0~30.0
| Defrost end setting point |  | DefrostCoreMng.DfrEndThrsh | 84 | 40085 |  | REAL | 0.0~30.0
| Environmental temperature setting point |  | DefrostCoreMng.AmbTempSetP | 85 | 40086 |  | REAL | -30.0~30.0
| Defrosting environment and coil temperature difference |  | DefrostCoreMng.DfrStartThrsh_DeltaT | 86 | 40087 |  | REAL | 1.0~30.0
| Defrost entry delay |  | DefrostCoreMng.DfrStartDT | 87 | 40088 |  | UINT | 0~90
| Minimize frost time |  | DefrostCoreMng.MinT_DFC | 88 | 40089 |  | UINT | 1-99
| Maximum frost time |  | DefrostCoreMng.MaxT_DFC | 89 | 40090 |  | UINT | 1~99
| Defrosting interval time |  | DefrostCoreMng.IntervalT_DFC | 90 | 40091 |  | UINT | 0-480
| Timed defrosting |  | DefrostCoreMng.Dfr_X_Hrs | 91 | 40092 |  | UINT | 1~999
| Start defrosting |  | DefrostCoreMng.DT_BeforeChgOver_DFC | 92 | 40093 |  | UINT | 0~99
| End defrosting |  | DefrostCoreMng.DT_AfterChgOver_DFC | 93 | 40094 |  | UINT | 0~99
| Drip water fan on time |  | DefrostCoreMng.DripT_DFC | 94 | 40095 |  | UINT | 0-999
| High voltage setting point |  | DefrostCoreMng.Dfr_CondFan_SetP | 95 | 40096 |  | REAL | 0.0~40.0
| Return difference |  | DefrostCoreMng.Dfr_CondFan_Diff | 96 | 40097 |  | REAL | 0.0~10.0
| High voltage setting point |  | Dfr_DscgP_offset | 97 | 40098 |  | REAL | 0.0~40.0
| Low voltage setting point |  | Dfr_SuctP_offset | 98 | 40099 |  | REAL | 0.0~30.0
（EVO OnBoard） | EEV1 MOP protection | Threshold | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.MOP_Thrsh.Val | 99 | 40100 |  | REAL | 0.0~999.0
|  | Integral time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.MOP_Ti.Val | 100 | 40101 |  | REAL | 0.0~999.0
|  | Alarm delay | EVD_Emb_1.Params_EVDEMB_1.EVD.Regulation.MOP_AlrmDT.Val | 101 | 40102 |  | INT | 0~999
| EEV1 | Prop.gain | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Kp.Val | 102 | 40103 |  | REAL | 0.0~999.0
|  | Integr time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Ti.Val | 103 | 40104 |  | REAL | 0.0~3200.0
|  | Deriv time | EVD_Emb_1.Params_EVDEMB_1.EVD.MainRegulation.PID_Td.Val | 104 | 40105 |  | REAL | 0.0~999.0
| Minimum EEVI opening when auxiliary valve is closed |  | EVD_Emb_1.EVD1_MinSteps | 105 | 40106 |  | INT | 0~480
| EEV2 | Prop.gain | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Kp.Val | 106 | 40107 |  | REAL | 0.0~999.0
|  | Integr time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Ti.Val | 107 | 40108 |  | REAL | 0.0~3200.0
|  | Deriv time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.MainRegulation.PID_Td.Val | 108 | 40109 |  | REAL | 0.0~999.0
| EEV2 MOP protection | Threshold | VD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondThrsh.Val | 109 | 40110 |  | REAL | 0.0~999.0
|  | Integral time | EVD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondTi.Val | 110 | 40111 |  | REAL | 0.0~999.0
|  | Alarm delay | EVD_Emb_1_2.Params_EVDEMB_1.EVD.AuxRegulation.HiTempCondAlrmDT.Val | 111 | 40112 |  | INT | 0-65536
（user mode） | 10℃＜ambient temp≤14℃ | Main valve superheat | SH_Set1_User[0] | 112 | 40113 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[0] | 113 | 40114 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[0] | 114 | 40115 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[0] | 115 | 40116 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[0] | 116 | 40117 |  | REAL | 0.0~999.0
| 5℃＜ambient temp≤9℃ | Main valve superheat | SH_Set1_User[1] | 117 | 40118 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[1] | 118 | 40119 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[1] | 119 | 40120 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[1] | 120 | 40121 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[1] | 121 | 40122 |  | REAL | 0.0~999.0
| 0℃＜ambient temp≤4℃ | Main valve superheat | SH_Set1_User[2] | 122 | 40123 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[2] | 123 | 40124 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[2] | 124 | 40125 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User2] | 125 | 40126 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[2] | 126 | 40127 |  | REAL | 0.0~999.0
| 一5℃＜ambient temp≤-1℃ | Main valve superheat | SH_Set1_User[3] | 127 | 40128 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[3] | 128 | 40129 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[3] | 129 | 40130 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[3] | 130 | 40131 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[3] | 131 | 40132 |  | REAL | 0.0~999.0
| 一10℃＜ambient temp≤一6℃ | Main valve superheat | SH_Set1_User[4] | 132 | 40133 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[4] | 133 | 40134 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[4] | 134 | 40135 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[4] | 135 | 40136 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[4] | 136 | 40137 |  | REAL | 0.0~999.0
| —15℃＜ambient temp≤一11℃ | Main valve superheat | SH_Set1_User[5] | 137 | 40138 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[5] | 138 | 40139 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[5] | 139 | 40140 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[5] | 140 | 40141 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[5] | 141 | 40142 |  | REAL | 0.0~999.0
| 一20℃＜ambient temp≤一16℃ | Main valve superheat | SH_Set1_User[6] | 142 | 40143 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[6] | 143 | 40144 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[6] | 144 | 40145 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[6] | 145 | 40146 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[6] | 146 | 40147 |  | REAL | 0.0~999.0
| ambient temp≤一21℃ | Main valve superheat | SH_Set1_User[7] | 147 | 40148 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[7] | 148 | 40149 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[7] | 149 | 40150 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[7] | 150 | 40151 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[7] | 151 | 40152 |  | REAL | 0.0~999.0
| 15℃＜ambient temp≤24℃ | Main valve superheat | SH_Set1_User[8] | 152 | 40153 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[8] | 153 | 40154 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[8] | 154 | 40155 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[8] | 155 | 40156 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[8] | 156 | 40157 |  | REAL | 0.0~999.0
| ambient temp＞25℃ | Main valve superheat | SH_Set1_User[9] | 157 | 40158 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[9] | 158 | 40159 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[9] | 159 | 40160 |  | INT | 0~100
|  | Steps of main valve after defrosting | EVD_DfrStep_User[9] | 160 | 40161 |  | INT | 0-480
|  | Maximum speed | MaxSpeedRpsUser[9] | 161 | 40162 |  | REAL | 0.0~999.0
| 33℃＜ambient temp≤37℃ | Main valve superheat | SH_Set1_User[10] | 162 | 40163 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[10] | 163 | 40164 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[10] | 164 | 40165 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[10] | 165 | 40166 |  | REAL | 0.0~999.0
| 30℃＜ambient temp≤32℃ | Main valve superheat | SH_Set1_User[11] | 166 | 40167 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[11] | 167 | 40168 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[11] | 168 | 40169 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[11] | 169 | 40170 |  | REAL | 0.0~999.0
| 26℃＜ambient temp≤29℃ | Main valve superheat | SH_Set1_User[12] | 170 | 40171 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[12] | 171 | 40172 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[12] | 172 | 40173 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[12] | 173 | 40174 |  | REAL | 0.0~999.0
| ambient temp≤25℃ | Main valve superheat | SH_Set1_User[13] | 174 | 40175 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[13] | 175 | 40176 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[13] | 176 | 40177 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[13] | 177 | 40178 |  | REAL | 0.0~999.0
| ambient temp＞38℃ | Main valve superheat | SH_Set1_User[14] | 178 | 40179 |  | REAL | -99.0~99.0
|  | Auxiliary valve superheat | SH_Set2_User[14] | 179 | 40180 |  | REAL | -99.0~99.0
|  | Start the initial opening of the main valve | StartEEV_OpRatio_User[14] | 180 | 40181 |  | INT | 0~100
|  | Maximum speed | MaxSpeedRpsUser[14] | 181 | 40182 |  | REAL | 0.0~999.0
| date | year | GeneralMng.YearIn | 182 | 40183 |  | UINT | 0~99
| date | month | GeneralMng.MonthIn | 183 | 40184 |  | UINT | 0~12
| date | day | GeneralMng.DayIn | 184 | 40185 |  | UINT | 0~31
| time | Hour | GeneralMng.HourIn | 185 | 40186 |  | UINT | 0~23
| time | branch | GeneralMng.MinuteIn | 186 | 40187 |  | UINT | 0~59
| week |  | GeneralMng.DayOfWeek | 187 | 40188 |  | UINT | 1~7
| Enable time zone switch on/off |  | En_SchedOnOff | 38 | 00039 | 0 | bool
| Enable timed change of setting points |  | En_Sch_Setp | 39 | 00040 | 1 | bool
| Enable synchronization |  | En_Date | 43 | 00044 | 0 | bool
| Unit mode | (On/Off) | UnitOn | 0 | 10001 |  | BOOL
B1 | Return water temperature | 0 | CW_InTemp | 188 | 40189 |  | REAL | ℃/℉
B2 | Outlet water temperature | 0 | CW_OutTemp | 189 | 40190 |  | REAL | ℃/℉
B3 | Ambient temp | 0 | AmbTemp | 190 | 40191 |  | REAL | ℃/℉
B4 | Exhaust temperature | 0 | DscgTemp | 191 | 40192 |  | REAL | ℃/℉
B5 | Suction temperature | 0 | SuctTemp | 192 | 40193 |  | REAL | ℃/℉
B6 | High pressure | 0 | DscgP | 193 | 40194 |  | REAL
B7 | Low pressure | 0 | SuctP | 194 | 40195 |  | REAL
B8 | Hot water temperature | 0 | CW_TankTemp | 195 | 40196 |  | REAL | ℃/℉
B9 | Coil temperature | 0 | CondsrCoilTemp | 196 | 40197 |  | REAL | ℃/℉
ID1 | Water flow switch | (On/Off) | InputsCheck.FlwSw_Din | 1 | 10002 |  | BOOL
ID2 | Emergency switch | (On/Off) | InputsCheck.RemoteOnOff_Din | 2 | 10003 |  | BOOL
ID3 | End signal switch | (On/Off) | InputsCheck.Terminal_Switch_Din | 3 | 10004 |  | BOOL
ID5 | Phase sequence protection | (On/Off) | InputsCheck.ProtSeqPh_Din | 4 | 10005 |  | BOOL
D01 | noble character |  | Outputs.DoutVal_1 | 5 | 10006 |  | BOOL
D02 | Low wind |  | Outputs.DoutVal_2 | 6 | 10007 |  | BOOL
D03 | Four way valve |  | Outputs.DoutVal_3 | 7 | 10008 |  | BOOL
D04 | Main engine water pump |  | Outputs.DoutVal_4 | 8 | 10009 |  | BOOL
D05 | Three way valve |  | Outputs.DoutVal_5 | 9 | 10010 |  | BOOL
D06 | Electric heating of crankshaft |  | Outputs.DoutVal_6 | 10 | 10011 |  | BOOL
D07 | Chassis electric heating |  | Outputs.DoutVal_7 | 11 | 10012 |  | BOOL
D09 | Electric heating |  | Outputs.DoutVal_9 | 12 | 10013 |  | BOOL
Y1 | Fan output |  | CondenserFan.y1_out | 197 | 40198 |  | REAL
Y3 | Water pump output |  | Pump_Aout | 198 | 40199 |  | REAL
| Speed regulation fan 1 output |  | CondenserFan.fan1_RPM_OUT_2 | 199 | 40200 |  | INT
| Speed control fan 1 feedback |  | CondenserFan.fan2_RPM_in_2 | 200 | 40201 |  | INT
| Speed regulation fan 2 output |  | CondenserFan.fan2_RPM_OUT_2 | 201 | 40202 |  | INT
| Speed control fan 2 feedback |  | CondenserFan.fan1_RPM_in_2 | 202 | 40203 |  | INT
| Required cap |  | BLDC_Mng.Info_BLDC1.Info_CompRequest | 203 | 40204 |  | REAL
| Actual cap |  | BLDC_Mng.Info_BLDC1.Info_ReqSpeedToPWRP | 204 | 40205 |  | REAL
| Actual speed |  | BLDC_Mng.Info_PWRP1.Info_RotorSpeed_rps | 205 | 40206 |  | REAL
| Evaporation temperature |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH_EvapTemp.Val | 206 | 40207 |  | REAL
| Electronic expansion valve opening |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | 207 | 40208 |  | INT
| Discharge Superheat |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.DscgSH.Val | 208 | 40209 |  | REAL
| Status | Drive status: | BLDC_Mng.Info_BLDC1.Info_HTZone | 209 | 40210 |  | INT |  | 0:ok 1:Controlled 2:limited
| Protection |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.ProtStatus.Val | 210 | 40211 |  | INT |  | 0: none 1：none 2：LowSH 3：lop 4:Mop 5:HiTcond
| Suction SH |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH.Val | 211 | 40212 |  | REAL
| Current operating mode of the unit |  | uniton_mode | 215 | 40216 |  | INT |  | 0: cooling 1: Heating 2: Hot water
| Unit switch on/off |  | OnOffUnitMng.KeybOnOff | 40 | 00041 | 0 | bool |  | 0: Off 1: On
| Current temperature |  | Temp_Target | 216 | 40217 |  | real
| Unit status |  | UnitStatus | 217 | 40218 |  | int | 0-11 | 0: Machine preparation; 1: Unit startup; 2: Alarm shutdown; 3: Network shutdown; 4: Monitoring shutdown; 5: Emergency shutdown; 6: Press the button to shut down; 7: Manual mode; 8: Unit antifreeze; 9: Networking switch; 10: Switching off; 11: High-temperature sterilization
| Water pump switch status |  | Pmp_On | 178 | 10179 |  | BOOL
| Compressor switch status |  | Comp_On | 179 | 10180 |  | BOOL
| Fan switch status |  | FanOn | 180 | 10181 |  | BOOL
| Alarm reset |  | AlrmResByBms | 41 | 00042 | 0 | BOOL
时钟管理 | Start on Monday: hour |  | TimezoneMng.On_Mon_Hour | 218 | 40219 |  | INT | 0-23
| Start on Monday: minutes |  | TimezoneMng.On_Mon_Min | 219 | 40220 |  | INT | 0-59
| On Tuesday: hour |  | TimezoneMng.On_Tue_Hour | 220 | 40221 |  | INT | 0-23
| Starting on Tuesday: minutes |  | TimezoneMng.On_Tue_Min | 221 | 40222 |  | INT | 0-59
| On Wednesday: hour |  | TimezoneMng.On_Wed_Hour | 222 | 40223 |  | INT | 0-23
| Starting on Wednesday: minutes |  | TimezoneMng.On_Wed_Min | 223 | 40224 |  | INT | 0-59
| Start on Thursday: hour |  | TimezoneMng.On_Thu_Hour | 224 | 40225 |  | INT | 0-23
| Start on Thursday: minutes |  | TimezoneMng.On_Thu_Min | 225 | 40226 |  | INT | 0-59
| Start on Friday: hour |  | TimezoneMng.On_Fri_Hour | 226 | 40227 |  | INT | 0-23
| Start on Friday: minutes |  | TimezoneMng.On_Fri_Min | 227 | 40228 |  | INT | 0-59
| Start on Saturday: hour |  | TimezoneMng.On_Sat_Hour | 228 | 40229 |  | INT | 0-23
| Start on Saturday: minutes |  | TimezoneMng.On_Sat_Min | 229 | 40230 |  | INT | 0-59
| Start on Sunday: hour |  | TimezoneMng.On_Sun_Hour | 230 | 40231 |  | INT | 0-23
| Start on Sunday: minutes |  | TimezoneMng.On_Sun_Min | 231 | 40232 |  | INT | 0-59
| Shutdown on Monday: hours |  | TimezoneMng.Off_Mon_Hour | 232 | 40233 |  | INT | 0-23
| Shutdown on Monday: minutes |  | TimezoneMng.Off_Mon_Min | 233 | 40234 |  | INT | 0-59
| Shutdown on Tuesday: hour |  | TimezOffeMng.Off_Tue_Hour | 234 | 40235 |  | INT | 0-23
| Shutdown on Tuesday: minutes |  | TimezOffeMng.Off_Tue_Min | 235 | 40236 |  | INT | 0-59
| Shutdown on Wednesday: hour |  | TimezOffeMng.Off_Wed_Hour | 236 | 40237 |  | INT | 0-23
| Shutdown on Wednesday: minutes |  | TimezOffeMng.Off_Wed_Min | 237 | 40238 |  | INT | 0-59
| Shutdown on Thursday: hour |  | TimezOffeMng.Off_Thu_Hour | 238 | 40239 |  | INT | 0-23
| Shutdown on Thursday: minutes |  | TimezOffeMng.Off_Thu_Min | 239 | 40240 |  | INT | 0-59
| Shutdown on Friday: hour |  | TimezOffeMng.Off_Fri_Hour | 240 | 40241 |  | INT | 0-23
| Shutdown on Friday: minutes |  | TimezOffeMng.Off_Fri_Min | 241 | 40242 |  | INT | 0-59
| Shutdown on Saturday: hour |  | TimezOffeMng.Off_Sat_Hour | 242 | 40243 |  | INT | 0-23
| Shutdown on Saturday: minutes |  | TimezOffeMng.Off_Sat_Min | 243 | 40244 |  | INT | 0-59
| Shutdown on Sunday: hour |  | TimezOffeMng.Off_Sun_Hour | 244 | 40245 |  | INT | 0-23
| Shutdown on Sunday: minutes |  | TimezOffeMng.Off_Sun_Min | 245 | 40246 |  | INT | 0-59
Time Zone 1 Management | Hour |  | TimezoneMng.TempHr1 | 246 | 40247 |  | INT | 0-23
| branch |  | TimezoneMng.TempMin1 | 247 | 40248 |  | INT | 0-59
| refrigeration |  | TimezoneMng.S_Set_Temp1 | 248 | 40249 |  | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp1 | 249 | 40250 |  | REAL | -99.0~99.0
Time Zone 2 Management | Hour |  | TimezoneMng.TempHr2 | 250 | 40251 |  | INT | 0-95
| branch |  | TimezoneMng.TempMin2 | 251 | 40252 |  | INT | 0-131
| refrigeration |  | TimezoneMng.S_Set_Temp2 | 252 | 40253 |  | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp2 | 253 | 40254 |  | REAL | -99.0~99.0
Time Zone 3 Management | Hour |  | TimezoneMng.TempHr3 | 254 | 40255 |  | INT | 0-167
| branch |  | TimezoneMng.TempMin3 | 255 | 40256 |  | INT | 0-203
| refrigeration |  | TimezoneMng.S_Set_Temp3 | 256 | 40257 |  | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp3 | 257 | 40258 |  | REAL | -99.0~99.0
Time Zone 4 Management | Hour |  | TimezoneMng.TempHr4 | 258 | 40259 |  | INT | 0-239
| branch |  | TimezoneMng.TempMin4 | 259 | 40260 |  | INT | 0-275
| refrigeration |  | TimezoneMng.S_Set_Temp4 | 260 | 40261 |  | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp4 | 261 | 40262 |  | REAL | -99.0~99.0
ID4 | Refrigeration linkage | (On/Off) | InputsCheck.CoolSw_Din | 181 | 10182 |  | BOOL
ID6 | Heating linkage | (On/Off) | InputsCheck.HeatSW_Din | 182 | 10183 |  | BOOL
DO8 | End water pump | (On/Off) | Outputs.DoutVal_8 | 183 | 10184 |  | BOOL
| on/off | DI4: Refrigeration linkage | InputsCheck.CoolSw_Logic | 45 | 00046 | 0 | BOOL
|  | DI5: Heating linkage | InputsCheck.HeatSW_Logic | 46 | 00047 | 1 | BOOL
|  | Speed regulating water pump | PumpMng.Enable_Ao_Pump | 47 | 00048 | 0 | BOOL | 0: Disable 1: Enable
|  | EEV2 manual mode | En_EVI_ManMode | 48 | 00049 | 0 | BOOL | 0: Disable 1: Enable
|  | EEV2 manual steps | EVI_ManSteps | 262 | 40263 |  | int | 0-480
|  | Manual low wind | ManDout1 | 49 | 00050 | 0 | BOOL
|  | Manual high wind | ManDout2 | 50 | 00051 | 0 | BOOL
|  | Fan grading windshield mode | fan_mode_bool | 51 | 00052 | 0 | BOOL | 0: Grading position 1: Grading
Fan Economy Mode | Cooling ambient temperature X-axis setting | X1 | X_CH[1] | 276 | 40277 |  | real | -99.9~99.9
|  | X2 | X_CH[2] | 277 | 40278 |  | real | -99.9~99.9
|  | X3 | X_CH[3] | 278 | 40279 |  | real | -99.9~99.9
|  | X4 | X_CH[4] | 279 | 40280 |  | real | -99.9~99.9
| Heating ambient temperature X-axis setting | X1 | X_Hp[1] | 280 | 40281 |  | real | -99.9~99.9
|  | X2 | X_Hp[2] | 281 | 40282 |  | real | -99.9~99.9
|  | X3 | X_Hp[3] | 282 | 40283 |  | real | -99.9~99.9
|  | X4 | X_Hp[4] | 283 | 40284 |  | real | -99.9~99.9
| Hot water ambient temperature X-axis setting | X1 | X_DHW[1] | 284 | 40285 |  | real | -99.9~99.9
|  | X2 | X_DHW[2] | 285 | 40286 |  | real | -99.9~99.9
|  | X3 | X_DHW[3] | 286 | 40287 |  | real | -99.9~99.9
|  | X4 | X_DHW[4] | 287 | 40288 |  | real | -99.9~99.9
| Cooling water temperature Y-axis setting point | Y2 | Y_CH[2] | 288 | 40289 |  | real | -99.9~99.9
|  | Y3 | Y_CH[3] | 289 | 40290 |  | real | -99.9~99.9
|  | Y4 | Y_CH[4] | 290 | 40291 |  | real | -99.9~99.9
| Heating water temperature Y-axis setting point | Y1 | Y_Hp[1] | 291 | 40292 |  | real | -99.9~99.9
|  | Y2 | Y_Hp[2] | 292 | 40293 |  | real | -99.9~99.9
|  | Y3 | Y_Hp[3] | 293 | 40294 |  | real | -99.9~99.9
| Hot water temperature Y-axis setting point | Y1 | Y_DHW[1] | 294 | 40295 |  | real | -99.9~99.9
|  | Y2 | Y_DHW[2] | 295 | 40296 |  | real | -99.9~99.9
|  | Y3 | Y_DHW[3] | 296 | 40297 |  | real | -99.9~99.9
|  | Enable mode switching based on ambient temperature | Enable_AmbTemp_Switch | 52 | 00053 | 1 | bool | 0: Disable 1: Enable
|  | Setting point for environmental temperature switching mode | Amb_switch_SetP | 297 | 40298 |  | real | 10.0~30.0
|  | Loop temperature switching mode return difference | Amb_switch_Offs | 298 | 40299 |  | real | 0.0~20.0
|  | Minimum start interval of water pump | MIN_pumpoffTime | 299 | 40300 |  | int | 1~99min
|  | Correction value of return water temperature | CW_InTemp_Offs | 300 | 40301 |  | real | 0.0~99.0
|  | Correction value of outlet water temperature | CW_OutTemp_Offs | 301 | 40302 |  | real | 0.0~99.0
|  | Ambient temp correction value | AmbTemp_Offs | 302 | 40303 |  | real | 0.0~99.0
|  | Exhaust temperature correction value | DscgTemp_Offs | 303 | 40304 |  | real | 0.0~99.0
|  | Correction value of suction temperature | SuctTemp_Offs | 304 | 40305 |  | real | 0.0~99.0
|  | High pressure correction value | DscgP_Offs | 305 | 40306 |  | real | 0.0~99.0
|  | Low pressure correction value | SuctP_Offs | 306 | 40307 |  | real | 0.0~99.0
|  | Correction value of hot water temperature | Water_Tank_Temp_Offs | 307 | 40308 |  | real | 0.0~99.0
|  | Correction value for coil temperature | CondsrCoilTemp_Offs | 308 | 40309 |  | real | 0.0~99.0
|  | Electronic expansion valve 2 opening | EVD_Emb_1_2.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | 309 | 40310 |  | int | 0-480
|  | High temperature differential load reduction deviation | DeltaTemp_Deload_SetP1 | 310 | 40311 |  | real | 0.0-99.0
|  | High temperature difference frequency limiting deviation | DeltaTemp_Deload_SetP2 | 311 | 40312 |  | real | 0.0-99.0
|  | High temperature difference frequency limiting exit deviation | DeltaTemp_Deload_SetP3 | 312 | 40313 |  | real | 0.0-99.0
|  | Deviation of high water outlet load reduction | OutletHighTemp_Deload_SetP1 | 313 | 40314 |  | real | 0.0-99.0
|  | High water outlet frequency limit deviation | OutletHighTemp_Deload_SetP2 | 314 | 40315 |  | real | 0.0-99.0
|  | Exit deviation of high water outlet frequency limit | OutletHighTemp_Deload_SetP3 | 315 | 40316 |  | real | 0.0-99.0
|  | Deviation of low effluent load reduction | OutletLowTemp_Deload_SetP1 | 316 | 40317 |  | real | 0.0-99.0
|  | Low water outlet frequency limit deviation | OutletLowTemp_Deload_SetP2 | 317 | 40318 |  | real | 0.0-99.0
|  | Low water outlet frequency limit exit deviation | OutletLowTemp_Deload_SetP3 | 318 | 40319 |  | real | 0.0-99.0
|  | Frequency reduction delay | Deloading_delay | 319 | 40320 |  | int | 0-99
|  | Frequency reduction status | Deload_Code | 320 | 40321 |  | int | 0: 1: High temperature differential frequency limit 2: Low water outlet frequency limit 3: High water outlet frequency limit
|  | Frequency reduction interval | Deload_Interval_time | 321 | 40322 |  | int | Unit: seconds
|  | Frequency reduction rate | Deload_rate | 322 | 40323 |  | real
|  | Enable high temperature differential frequency limiting | Enable_DeltaTemp_Limit | 184 | 10185 |  | bool
|  | Enable low water outlet frequency limiting | Enable_LowOutletTemp_Limit | 185 | 10186 |  | bool
|  | Enable high water outlet frequency limiting | Enable_highOutletTemp_Limit | 186 | 10187 |  | bool
|  | Electric heating control | En_AuxHeat | 323 | 40324 |  | INT | 0: Disabled 1: Hot water 2: Floor heating 3: Shared
|  | Antifreeze requirements | Anti_CompReq | 324 | 40325 |  | real
|  | First level antifreeze enable | Enable_Antifreeze_Prevent_first | 53 | 00054 | 1 | bool | 0: Disable 1: Enable
|  | Secondary antifreeze enable | Enable_Antifreeze_Prevent_sec | 54 | 00055 | 0 | bool | 0: Disable 1: Enable
|  | Program version number 1 | GeneralMng.CurrVer.X | 325 | 40326 |  | INT
|  | Program version number 2 | GeneralMng.CurrVer.Y | 326 | 40327 |  | INT
|  | Program version number 3 | GeneralMng.CurrVer.Z | 327 | 40328 |  | INT
|  | Unit Model Code 1 | GeneralMng.UnitType_A | 328 | 40329 |  | INT
|  | Unit Model Code 2 | GeneralMng.UnitType_B | 329 | 40330 |  | INT
|  | Delayed start of the water pump for three minutes during fault standby | Alarm_pumpoff_Time | 330 | 40331 |  | int | min
|  | During normal standby, delay starting the water pump for three minutes | Unit_StandBy_Anti_Delay | 331 | 40332 |  | INT | min
|  | Switch from station to hot water mode and enable hot water demand | Enable_HotWater_mode_switch | 55 | 00056 | 0 | bool | 0: Disable 1: Enable
|  | Input and output frequency converter default value | BLDC_Mng.MiscMng_PWRP1.Mng_WriteDefault | 332 | 40333 |  | int | 0: No 1: Yes
|  | Restore default values | En_WipeMem | 57 | 00058 |  | bool | 0: No 1: Yes
|  | Frequency converter power | BLDC_Mng.Info_PWRP1.Info_MotPwr | 333 | 40334 |  | real
|  | Frequency converter voltage | BLDC_Mng.Info_PWRP1.Info_MotV | 334 | 40335 |  | int
|  | Frequency converter current | BLDC_Mng.Info_PWRP1.Info_MotA | 335 | 40336 |  | real
|  | Refrigeration point compensation | Cool_SetPCompensated_enable | 110 | 00111 |  | bool | 0: Disable 1: Enable
|  | Heating point compensation | Heat_SetPCompensated_enable | 111 | 00112 |  | bool | 0: Disable 1: Enable
|  | Hot water point compensation | W_TankSetPCompensated_enable | 112 | 00113 |  | bool | 0: Disable 1: Enable
|  | Swimming pool switch status | POOL_HeatSw_Din | 113 | 00114 |  | bool | 0: Closed 1: Open
|  | Heating mode enables swimming pool function | En_pool_heat_heat | 114 | 00115 |  | bool | 0: Disable 1: Enable
|  | Hot water mode enables swimming pool function | En_pool_heat_hot | 115 | 00116 |  | bool | 0: Disable 1: Enable
|  | Heating+hot water mode enables swimming pool function | En_pool_heat_heathot | 116 | 00117 |  | bool | 0: Disable 1: Enable
| alarm no. |  | Description | index | modbus |  | data type |  | Description
| AL001 |  | Too many mem writings | 13 | 10014 | 1 | BOOL |  | Frequent writing of storage type variables
| AL002 |  | Retain mem write error | 14 | 10015 | 1 | BOOL |  | Frequent write error alarms for stored variables
| AL003 |  | Inlet probe error | 15 | 10016 | 1 | BOOL |  | Inlet temperature probe faulty or offline
| AL004 |  | Outlet probe error | 16 | 10017 | 1 | BOOL |  | Faulty or offline outlet temperature probe
| AL005 |  | Ambient probe error | 17 | 10018 | 1 | BOOL |  | Ambient temp probe malfunction or offline
| AL006 |  | Condenser coil temp | 18 | 10019 | 1 | BOOL |  | Condensation coil temperature probe faulty or offline
| AL007 |  | Water flow switch | 19 | 10020 | 1 | BOOL |  | Water flow switch alarm
| AL008 |  | Phase sequ.prot.alarm | 20 | 10021 | 1 | BOOL |  | Phase sequence protection switch alarm
| AL009 |  | Unit work hour warning | 21 | 10022 | 1 | BOOL |  | Unit working time warning
| AL010 |  | Pump work hour warning | 22 | 10023 | 1 | BOOL |  | Water pump working time warning
| AL011 |  | Comp.work hour warning | 23 | 10024 | 1 | BOOL |  | Compressor working time warning
| AL012 |  | Cond.fan work hourWarn | 24 | 10025 | 1 | BOOL |  | Working time of condensing fan
| AL013 |  | Low superheat - Vlv.A | 25 | 10026 | 1 | BOOL |  | EEV valve A low superheat alarm
| AL014 |  | Low superheat - Vlv.B | 26 | 10027 | 1 | BOOL |  | EEV valve B low superheat alarm
| AL015 |  | LOP - Vlv.A | 27 | 10028 | 1 | BOOL |  | EEV valve A LOP alarm
| AL016 |  | LOP - Vlv.B | 28 | 10029 | 1 | BOOL |  | EEV valve B LOP alarm
| AL017 |  | MOP - Vlv.A | 29 | 10030 | 1 | BOOL |  | EEV valve A MOP alarm
| AL018 |  | MOP - Vlv.B | 30 | 10031 | 1 | BOOL |  | EEV valve B MOP alarm
| AL019 |  | Motor error - Vlv.A | 31 | 10032 | 1 | BOOL |  | EEV valve A alarm
| AL020 |  | Motor error - Vlv.B | 32 | 10033 | 1 | BOOL |  | EEV valve B alarm
| AL021 |  | Low suct.temp. - Vlv.A | 33 | 10034 | 1 | BOOL |  | EEV valve A low suction temperature alarm
| AL022 |  | Low suct.temp. - Vlv.B | 34 | 10035 | 1 | BOOL |  | EEV valve B low suction temperature alarm
| AL023 |  | High condens.temp.EVD | 35 | 10036 | 1 | BOOL |  | EEV high condensation temperature alarm
| AL024 |  | Probe S1 error EVD | 36 | 10037 | 1 | BOOL |  | EEV S1 probe alarm
| AL025 |  | Probe S2 error EVD | 37 | 10038 | 1 | BOOL |  | EEV S2 probe alarm
| AL026 |  | Probe S3 error EVD | 38 | 10039 | 1 | BOOL |  | EEV S3 probe alarm
| AL027 |  | Probe S4 error EVD | 39 | 10040 | 1 | BOOL |  | EEV S4 probe alarm
| AL028 |  | Battery discharge EVD | 40 | 10041 | 1 | BOOL |  | EEV battery failure
| AL029 |  | EEPROM alarm EVD | 41 | 10042 | 1 | BOOL |  | EEV EEPROM alarm
| AL030 |  | Incomplete closing EVD | 42 | 10043 | 1 | BOOL |  | EEV not fully closed alarm
| AL031 |  | Emergency closing EVD | 43 | 10044 | 1 | BOOL |  | EEV emergency shutdown alarm
| AL032 |  | FW not compatible EVD | 44 | 10045 | 1 | BOOL |  | EEV FW version mismatch
| AL033 |  | Config. error EVD | 45 | 10046 | 1 | BOOL |  | EEV configuration error
| AL034 |  | EVD Driver offline | 46 | 10047 | 1 | BOOL |  | EEV offline alarm
| AL035 |  | BLDC-alarm:High startup DeltaP | 47 | 10048 | 1 | BOOL |  | BLDC - Starting pressure difference too high
| AL036 |  | BLDC-alarm:Compressor shut off | 48 | 10049 | 1 | BOOL |  | BLDC Compressor Off
| AL037 |  | BLDC-alarm:Out of Envelope | 49 | 10050 | 1 | BOOL |  | BLDC - out of operating range
| AL038 |  | BLDC-alarm:Starting fail wait | 50 | 10051 | 1 | BOOL |  | BLDC Compressor Start Failure
| AL039 |  | BLDC-alarm:Starting fail exceeded | 51 | 10052 | 1 | BOOL |  | BLDC Compressor Start Failure
| AL040 |  | BLDC-alarm:Low delta pressure | 52 | 10053 | 1 | BOOL |  | BLDC Low Pressure Differential
| AL041 |  | BLDC-alarm:High discarge gas temp | 53 | 10054 | 1 | BOOL |  | BLDC High Exhaust Temperature
| AL042 |  | Envelope-alarm:High compressor ratio | 54 | 10055 | 1 | BOOL |  | Envelope High voltage ratio
| AL043 |  | Envelope-alarm:High discharge press. | 55 | 10056 | 1 | BOOL |  | Envelope - High exhaust pressure
| AL044 |  | Envelope-alarm:High current | 56 | 10057 | 1 | BOOL |  | Envelope - High current
| AL045 |  | Envelope-alarm:High suction pressure | 57 | 10058 | 1 | BOOL |  | Envelope - High suction pressure
| AL046 |  | Envelope-alarm:Low compressor ratio | 58 | 10059 | 1 | BOOL |  | Envelope - Low voltage ratio
| AL047 |  | Envelope-alarm:Low pressure diff. | 59 | 10060 | 1 | BOOL |  | Envelope - Low pressure difference
| AL048 |  | Envelope-alarm:Low discharge pressure | 60 | 10061 | 1 | BOOL |  | Envelope - Low exhaust pressure
| AL049 |  | Envelope-alarm:Low suction pressure | 61 | 10062 | 1 | BOOL |  | Envelope - Low suction pressure
| AL050 |  | Envelope-alarm:High discharge temp. | 62 | 10063 | 1 | BOOL |  | Envelope - High exhaust temperature
| AL051 |  | Power+ alarm:01-Overcurrent | 63 | 10064 | 1 | BOOL |  | Power+01- Overcurrent
| AL052 |  | Power+ alarm:02-Motor overload | 64 | 10065 | 1 | BOOL |  | Power+02- Motor overload
| AL053 |  | Power+ alarm:03-DCbus overvoltage | 65 | 10066 | 1 | BOOL |  | Power+03-DCbus overvoltage
| AL054 |  | Power+ alarm:04-DCbus undervoltage | 66 | 10067 | 1 | BOOL |  | Power+04-DCbus undervoltage
| AL055 |  | Power+ alarm:05-Drive overtemp. | 67 | 10068 | 1 | BOOL |  | Power+05- Frequency converter overheating
| AL056 |  | Power+ alarm:06-Drive undertemp. | 68 | 10069 | 1 | BOOL |  | Power+06- Inverter under temperature
| AL057 |  | Power+ alarm:07-Overcurrent HW | 69 | 10070 | 1 | BOOL |  | Power+07- Overcurrent HW
| AL058 |  | Power+ alarm:08-Motor overtemp. | 70 | 10071 | 1 | BOOL |  | Power+08- Motor overheating
| AL059 |  | Power+ alarm:09-IGBT module error | 71 | 10072 | 1 | BOOL |  | Power+09-IGBT module failure
| AL060 |  | Power+ alarm:10-CPU error | 72 | 10073 | 1 | BOOL |  | Power+10 CPU failure
| AL061 |  | Power+ alarm:11-Parameter default | 73 | 10074 | 1 | BOOL |  | Power+11- Missing parameter
| AL062 |  | Power+ alarm:12-DCbus ripple | 74 | 10075 | 1 | BOOL |  | Power+12- Bus voltage fluctuation
| AL063 |  | Power+ alarm:13-Data comm. Fault | 75 | 10076 | 1 | BOOL |  | Power+13- Data communication failure
| AL064 |  | Power+ alarm:14-Thermistor fault | 76 | 10077 | 1 | BOOL |  | Power+14- Thermistor fault
| AL065 |  | Power+ alarm:15-Autotuning fault | 77 | 10078 | 1 | BOOL |  | Power+15- automatic adjustment fault
| AL066 |  | Power+ alarm:16-Drive disabled | 78 | 10079 | 1 | BOOL |  | Power+16- frequency converter disabled
| AL067 |  | Power+ alarm:17-Motor phase fault | 79 | 10080 | 1 | BOOL |  | Power+17- Motor phase sequence fault
| AL068 |  | Power+ alarm:18-Internal fan fault | 80 | 10081 | 1 | BOOL |  | Power+18- Fan fault
| AL069 |  | Power+ alarm:19-Speed fault | 81 | 10082 | 1 | BOOL |  | Power+19- Speed fault
| AL070 |  | Power+ alarm:20-PFC module error | 82 | 10083 | 1 | BOOL |  | Power+20-PFC module failure
| AL071 |  | Power+ alarm:21-PFC overvoltage | 83 | 10084 | 1 | BOOL |  | Power+21-PFC overvoltage
| AL072 |  | Power+ alarm:22-PFC undervoltage | 84 | 10085 | 1 | BOOL |  | Power+22-PFC undervoltage
| AL073 |  | Power+ alarm:23-STO DetectionError | 85 | 10086 | 1 | BOOL |  | Power+23-STO error detection
| AL074 |  | Power+ alarm:24-STO DetectionError | 86 | 10087 | 1 | BOOL |  | Power+24-STO error detection
| AL075 |  | Power+ alarm:25-Ground fault | 87 | 10088 | 1 | BOOL |  | Power+25- Ground wire fault
| AL076 |  | Power+ alarm:26-Internal error 1 | 88 | 10089 | 1 | BOOL |  | Power+26-CPU synchronization error 1
| AL077 |  | Power+ alarm:27-Internal error 2 | 89 | 10090 | 1 | BOOL |  | Power+27-CPU synchronization error 2
| AL078 |  | Power+ alarm:28-Drive overload | 90 | 10091 | 1 | BOOL |  | Power+28- Inverter overload
| AL079 |  | Power+ alarm:29-uC safety fault | 91 | 10092 | 1 | BOOL |  | Power+29：uC safety fault
| AL080 |  | Power+ alarm:98-Unexpected restart | 92 | 10093 | 1 | BOOL |  | Power+98：Unexpected restart
| AL081 |  | Power+ alarm:99-Unexpected stop | 93 | 10094 | 1 | BOOL |  | Power+99：Unexpected stop
| AL082 |  | Power+ safety alarm:01-Current meas.fault | 94 | 10095 | 1 | BOOL |  | Power+ safety alarm:01-Current meas.fault
| AL083 |  | Power+ safety alarm:02-Current unbalanced | 95 | 10096 | 1 | BOOL |  | Power+ safety alarm:02-Current unbalanced
| AL084 |  | Power+ safety alarm:03-Over current | 96 | 10097 | 1 | BOOL |  | Power+ safety alarm:03-Over current
| AL085 |  | Power+ safety alarm:04-STO alarm | 97 | 10098 | 1 | BOOL |  | Power+ safety alarm:04-STO alarm
| AL086 |  | Power+ safety alarm:05-STO hardware alarm | 98 | 10099 | 1 | BOOL |  | Power+ safety alarm:05-STO hardware alarm
| AL087 |  | Power+ safety alarm:06-PowerSupply missing | 99 | 10100 | 1 | BOOL |  | Power+ safety alarm:06-PowerSupply missing
| AL088 |  | Power+ safety alarm:07-HW fault cmd.buffer | 100 | 10101 | 1 | BOOL |  | Power+ safety alarm:07-HW fault cmd.buffer
| AL089 |  | Power+ safety alarm:08-HW fault heater c. | 101 | 10102 | 1 | BOOL |  | Power+ safety alarm:08-HW fault heater c.
| AL090 |  | Power+ safety alarm:09-Data comm. Fault | 102 | 10103 | 1 | BOOL |  | Power+ safety alarm:09-Data comm. Fault
| AL091 |  | Power+ safety alarm:10-Compr. stall detect | 103 | 10104 | 1 | BOOL |  | Power+ safety alarm:10-Compr. stall detect
| AL092 |  | Power+ safety alarm:11-DCbus over current | 104 | 10105 | 1 | BOOL |  | Power+ safety alarm:11-DCbus over current
| AL093 |  | Power+ safety alarm:12-HWF DCbus current | 105 | 10106 | 1 | BOOL |  | Power+ safety alarm:12-HWF DCbus current
| AL094 |  | Power+ safety alarm:13-DCbus voltage | 106 | 10107 | 1 | BOOL |  | Power+ safety alarm:13-DCbus voltage
| AL095 |  | Power+ safety alarm:14-HWF DCbus voltage | 107 | 10108 | 1 | BOOL |  | Power+ safety alarm:14-HWF DCbus voltage
| AL096 |  | Power+ safety alarm:15-Input voltage | 108 | 10109 | 1 | BOOL |  | Power+ safety alarm:15-Input voltage
| AL097 |  | Power+ safety alarm:16-HWF input voltage | 109 | 10110 | 1 | BOOL |  | Power+ safety alarm:16-HWF input voltage
| AL098 |  | Power+ safety alarm:17-DCbus power alarm | 110 | 10111 | 1 | BOOL |  | Power+ safety alarm:17-DCbus power alarm
| AL099 |  | Power+ safety alarm:18-HWF power mismatch | 111 | 10112 | 1 | BOOL |  | Power+ safety alarm:18-HWF power mismatch
| AL100 |  | Power+ safety alarm:19-NTC over temp. | 112 | 10113 | 1 | BOOL |  | Power+ safety alarm:19-NTC over temp.
| AL101 |  | Power+ safety alarm:20-NTC under temp. | 113 | 10114 | 1 | BOOL |  | Power+ safety alarm:20-NTC under temp.
| AL102 |  | Power+ safety alarm:21-NTC fault | 114 | 10115 | 1 | BOOL |  | Power+ safety alarm:21-NTC fault
| AL103 |  | Power+ safety alarm:22-HWF sync fault | 115 | 10116 | 1 | BOOL |  | Power+ safety alarm:22-HWF sync fault
| AL104 |  | Power+ safety alarm:23-Invalid parameter | 116 | 10117 | 1 | BOOL |  | Power+ safety alarm:23-Invalid parameter
| AL105 |  | Power+ safety alarm:24-FW fault | 117 | 10118 | 1 | BOOL |  | Power+ safety alarm:24-FW fault
| AL106 |  | Power+ safety alarm:25-HW fault | 118 | 10119 | 1 | BOOL |  | Power+ safety alarm:25-HW fault
| AL107 |  | Power+ safety alarm:26-reseved | 119 | 10120 | 1 | BOOL |  | Power+ safety alarm:26-reseved
| AL108 |  | Power+ safety alarm:27-reseved | 120 | 10121 | 1 | BOOL |  | Power+ safety alarm:27-reseved
| AL109 |  | Power+ safety alarm:28-reseved | 121 | 10122 | 1 | BOOL |  | Power+ safety alarm:28-reseved
| AL110 |  | Power+ safety alarm:29-reseved | 122 | 10123 | 1 | BOOL |  | Power+ safety alarm:29-reseved
| AL111 |  | Power+ safety alarm:30-reseved | 123 | 10124 | 1 | BOOL |  | Power+ safety alarm:30-reseved
| AL112 |  | Power+ safety alarm:31-reseved | 124 | 10125 | 1 | BOOL |  | Power+ safety alarm:31-reseved
| AL113 |  | Power+ safety alarm:32-reseved | 125 | 10126 | 1 | BOOL |  | Power+ safety alarm:32-reseved
| AL114 |  | Power+ alarm:Power+ offline | 126 | 10127 | 1 | BOOL |  | Inverter offline alarm
| AL115 |  | EEV alarm:Low superheat | 127 | 10128 | 1 | BOOL |  | EEV low superheat alarm
| AL116 |  | EEV alarm:LOP | 128 | 10129 | 1 | BOOL |  | EEV LOP alarm
| AL117 |  | EEV alarm:MOP | 129 | 10130 | 1 | BOOL |  | EEV MOP alarm
| AL118 |  | EEV alarm:High condens.temp. | 130 | 10131 | 1 | BOOL |  | EEV high condensation temperature alarm
| AL119 |  | EEV alarm:Low suction temp. | 131 | 10132 | 1 | BOOL |  | EEV low suction temperature alarm
| AL120 |  | EEV alarm:Motor error | 132 | 10133 | 1 | BOOL |  | EEV motor fault
| AL121 |  | EEV alarm:Self Tuning | 133 | 10134 | 1 | BOOL |  | EEV from  PID error
| AL122 |  | EEV alarm:Emergency closing | 134 | 10135 | 1 | BOOL |  | EEV emergency shutdown alarm
| AL123 |  | EEV alarm:Temperature delta | 135 | 10136 | 1 | BOOL |  | EEV temperature difference protection
| AL124 |  | EEV alarm:Pressure delta | 136 | 10137 | 1 | BOOL |  | EEV differential pressure protection
| AL125 |  | EEV alarm:Param.range error | 137 | 10138 | 1 | BOOL |  | EEV range error
| AL126 |  | EEV alarm:ServicePosit% err | 138 | 10139 | 1 | BOOL |  | EEV position signal error
| AL127 |  | EEV alarm:ValveID pin error | 139 | 10140 | 1 | BOOL |  | EEV serial number error
| AL128 |  | Low press alarm | 140 | 10141 | 1 | BOOL |  | Low pressure alarm
| AL129 |  | High press alarm | 141 | 10142 | 1 | BOOL |  | High voltage alarm
| AL130 |  | Disc.temp.probe error | 142 | 10143 | 1 | BOOL |  | Exhaust temperature probe alarm
| AL131 |  | Suct.temp.probe error | 143 | 10144 | 1 | BOOL |  | Suction temperature probe alarm
| AL132 |  | Disc.press.probe error | 144 | 10145 | 1 | BOOL |  | Exhaust pressure probe alarm
| AL133 |  | Suct.press.probe error | 145 | 10146 | 1 | BOOL |  | Suction pressure probe alarm
| AL134 |  | Tank temp.probe error | 146 | 10147 | 1 | BOOL |  | Water tank temperature probe alarm
| AL135 |  | EVI SuctT.probe error | 147 | 10148 | 1 | BOOL |  | EVI suction temperature probe alarm
| AL136 |  | EVI SuctP.probe error | 148 | 10149 | 1 | BOOL |  | EVI suction pressure probe alarm
| AL137 |  | Flow switch alarm | 149 | 10150 | 1 | BOOL |  | Water flow switch alarm
| AL138 |  | High temp. alarm | 150 | 10151 | 1 | BOOL |  | High water outlet temperature alarm
| AL139 |  | Low temp. alarm | 151 | 10152 | 1 | BOOL |  | Low water outlet temperature alarm
| AL140 |  | Temp.delta alarm | 152 | 10153 | 1 | BOOL |  | Inlet and outlet water temperature difference alarm
| AL141 |  | EVI alarm:Param.range error | 153 | 10154 | 1 | BOOL |  | EVI Range Error
| AL142 |  | EVI alarm:Low superheat | 154 | 10155 | 1 | BOOL |  | EVI low superheat alarm
| AL143 |  | EVI alarm:LOP | 155 | 10156 | 1 | BOOL |  | EVI LOP alarm
| AL144 |  | EVI alarm:MOP | 156 | 10157 | 1 | BOOL |  | EVI MOP alarm
| AL145 |  | EVI alarm:High condens.temp. | 157 | 10158 | 1 | BOOL |  | EVI high condensation temperature alarm
| AL146 |  | EVI alarm:Low suction temp. | 158 | 10159 | 1 | BOOL |  | EVI low suction temperature alarm
| AL147 |  | EVI alarm:Motor error | 159 | 10160 | 1 | BOOL |  | EVI motor malfunction
| AL148 |  | EVI alarm:Self Tuning | 160 | 10161 | 1 | BOOL |  | EVI adaptive PID error
| AL149 |  | EVI alarm:Emergency closing | 161 | 10162 | 1 | BOOL |  | EVI emergency shutdown
| AL150 |  | EVI alarm:ServicePosit% err | 162 | 10163 | 1 | BOOL |  | EVI position signal error
| AL151 |  | EVI alarm:ValveID pin error | 163 | 10164 | 1 | BOOL |  | EVI serial number error
| AL152 |  | Supply power error | 164 | 10165 | 1 | BOOL |  | Power frequency fluctuation alarm
| AL153 |  | Fan1 fault | 165 | 10166 | 1 | BOOL |  | Speed control fan 1 malfunction
| AL154 |  | Fan2 fault | 166 | 10167 | 1 | BOOL |  | Speed control fan 2 malfunction
| AL155 |  | Fans Offline | 167 | 10168 | 1 | BOOL |  | Speed control fan communication offline
| AL165 |  | Slave1 Offline | 168 | 10169 | 1 | BOOL |  | 1 # Slave offline
| AL166 |  | Master Offline | 169 | 10170 | 1 | BOOL |  | Host offline
| AL167 |  | Slave2 Offline | 170 | 10171 | 1 | BOOL |  | 2 # slave offline
| AL168 |  | Slave3 Offline | 171 | 10172 | 1 | BOOL |  | 3 # slave offline
| AL169 |  | Slave4 Offline | 172 | 10173 | 1 | BOOL |  | 4 # slave offline
| AL170 |  | Slave5 Offline | 173 | 10174 | 1 | BOOL |  | 5 # slave offline
| AL171 |  | Slave6 Offline | 174 | 10175 | 1 | BOOL |  | 6 # slave offline
| AL172 |  | Slave7 Offline | 175 | 10176 | 1 | BOOL |  | 7 # slave offline
| AL173 |  | Slave8 Offline | 176 | 10177 | 1 | BOOL |  | 8 # slave offline
| AL174 |  | Slave9 Offline | 177 | 10178 | 1 | BOOL |  | 9 # slave offline
2022.01.25增加：
| 融霜标识 |  | Run_DFC | 237 | 10238 | 1 | bool | 融霜显示：0为未融霜，1为正在融霜
| AL176 |  | Al_LowAmbTemp.Active | 239 | 10240 | 1 | bool | ambient temp过低保护报警
| 融霜参数判断环温区间设点1 |  | DefrostCoreMng.Set_AmbTempRange[0] | 478 | 40479 | 1 | real | -99.9~99.9
| 融霜参数判断环温区间设点2 |  | DefrostCoreMng.Set_AmbTempRange[1] | 479 | 40480 | 1 | real | -99.9~99.9
| 环温低于区间设点1的融霜进入温差设点 |  | DefrostCoreMng.Set_DfrStartDeltaTemp[0] | 480 | 40481 | 1 | real | 0.0~99.9
| 环温介于区间设点1和2之间的融霜进入温差设点 |  | DefrostCoreMng.Set_DfrStartDeltaTemp[1] | 481 | 40482 | 1 | real | 0.0~99.9
| 环温低于区间设点1的融霜间隔时间设点 |  | DefrostCoreMng.Set_DfrIntervalTime[0] | 482 | 40483 | 1 | uint | 0~999
| 环温介于区间设点1和2之间的融霜间隔时间设点 |  | DefrostCoreMng.Set_DfrIntervalTime[1] | 483 | 40484 | 1 | uint | 0~999
| 长时间未融霜时间设定：低温运行时间设定（分钟） |  | DefrostCoreMng.DfrStartTime1 | 484 | 40485 | 1 | int | 0~999
| 长时间未融霜时间设定：压缩机运行时间设定（分钟） |  | DefrostCoreMng.DfrStartTime2 | 485 | 40486 | 1 | int | 0~999
| 低环温报警设点 |  | AlarmMng.LowAmbTempSetP | 486 | 40487 | 1 | real | -50.0~10.0
| 低环温报警回差 |  | AlarmMng.LowAmbTempDiff | 487 | 40488 | 1 | real | -20.0~20.0
| 当前设点显示 |  | TempSetP | 488 | 40489 | 1 | real
2022.03.01增加：
| 主阀退出最小开度稳定时间 |  | EVD_Emb_1.ExitMinStepDT | 489 | 40490 | 1 | int | 0~99
| 辅阀开时主阀最小开度 |  | EVD_Emb_1.EVD1_MinSteps_2 | 490 | 40491 | 1 | int | 0~480
2022.03.17增加：
| 低环温高水温补偿：低环温设定值 |  | InputsCheck.AmbTemp_SetP_1 | 339 | 40340 | 1 | real | -35.0~20.0
| 低环温高水温补偿：高水温设定值 |  | InputsCheck.HighWaterTemp_SetP | 340 | 40341 | 1 | real | 35.0~45.0
| 低环温低压补偿:低环温设定值 |  | InputsCheck.AmbTemp_SetP_2 | 341 | 40342 | 1 | real | -35.0~0.0
| 低环温低压补偿:低压补偿值 |  | InputsCheck.SuctP_Compensation_SetP | 342 | 40343 | 1 | real | 0.00~9.99
2022.03.22增加：
| 增焓阀初始开度控制：出水温度设点 |  | EVD_Emb_1_2.StartEEV_OpRatio_CWOutTempSetP | 343 | 40344 | 1 | real | 0.0~99.9
| 增焓阀初始开度控制：低出水温度初始开度设定 |  | EVD_Emb_1_2.StartEEV_OpRatio_SetP_1 | 344 | 40345 | 1 | int | 0~100
| 增焓阀初始开度控制：高出水温度初始开度设定 |  | EVD_Emb_1_2.StartEEV_OpRatio_SetP_2 | 345 | 40346 | 1 | int | 0~100